| 12.01.2024. | Nr. 2.5/2024/170 |
| --- | --- |
| Uz | Nr. |

To the tenderers of the negotiated procedure No. AST2023/149-ES

Subject: Negotiation procedure No. AST2023/149-ES - answers to the tenderer's requests for clarifications

Herewith we provide answers to the tenderers' requests for clarifications regarding the negotiation procedures regulations No. AST2023/149-ES " Supply of 110/21/10.5 kV 25 MVA transformer to the substation "TEC-2"":

Tenderer's request for clarification No.1:

At page 52, second page of technical specifications it is mentioned that offered type of transformer is tested with full short-circuit current, and it is indicated as required. In any other tender in any country, including Latvia, it was never obligatory, please confirm that testing with full short-circuit current is not required.

Clarification No.1

Customer revises the technical specification's positions:

| Offered type of transformer is tested with full short-circuit current | Yes |  |
| --- | --- | --- |

as follows:

| Offered type of transformer is tested with full short-circuit current | Yes / no |  |
| --- | --- | --- |

Any answer is acceptable and will be not considered as non-compliance with technical requirements.

Please pay attention that tenderers must submit the following information:

| Manufacturer shall provide written description of the short circuit's method. Moreover, the validity of the used method should be proved by tests made to similar constructions and at same stress levels used in the design. | Please attach |  |
| --- | --- | --- |
| Type test certificate, acc. IEC 60076-5, 2006, the short circuit withstand tests for transformers of category II with voltage level 110 kV (acc. to IEC 6076-5 point 3.2.2). Test must be made within last ten years. Test shall be carried out by independent laboratory, notified as EA (European Cooperation for Accreditation). | Please attach to the tender |  |

Tenderer's request for clarification No.2:

In the clarification from you (Vestule), at point 4.4.3. we would like to add "but no longer than 2 months after successful FAT". So point 4.4.3 will become;

Upon arrival of the Goods at the point of delivery and upon installation of the transformer on the foundations, as evidenced by the mutual signature of the deed of transfer-acceptance referred to in Clause 7.2.2 of the Agreement, purchaser shall pay 90% of the indexed Contract price after mutual signature of the deed of transfer-acceptance but no longer than 2 months after successful FAT, within 30 calendar days after receipt of corresponding invoice for the Goods delivered from the supplier.

Clarification No.2

Customer cannot accept the above-mentioned Tenderer's proposal.

Kind regards,

| Iepirkumu daļas vadītājs | Kristīne Graudumniece |
| --- | --- |

Gavronskis

juris.gavronskis@ast.lv