Annex 13

Procurement ID No AST2024/91

Joint Stock Company "Augstsprieguma tīkls"

open procedure

"Supply of electrical equipment to the 110 kV substation "Līvāni""

(ID No AST2024/91)

Lot 4 "Relay protection and automation (RAA) and dispatching system (DVS) equipment for 110 kV substation"

Technical specification, technical offer (updated 30.10.2024.)

Tenderer  _______

# Relay protection for substation “Līvāni” 110kV switchyard and line’s remote ends.

Relay protection at substation “Līvāni” for:

- two 110kV lines;

- busbars with bus disconnectors.

- two 110/20/6kV transformers;

All the paragraphs are obligatory requirements of the Purchaser (hereinafter – the Customer) unless there is remark “Informative part”.

## General requirements.

| Required: |  |  | Offered: |
| --- | --- | --- | --- |
| The bid shall include all necessary hardware (cases etc.) and software for functions and features specified in Items 1.1-1.7 together with all necessary auxiliary relays and connection units. |  |  |  |
| At least 5 licenses for all used software shall be included |  |  |  |
| The Customer has rights to use any functionality that is available in the relays. Time for commissioning shall be included in overall commissioning time given bellow. |  |  |  |
| Delivered software shall be indicated in the invoice |  |  |  |
| In the tender technical specification form should be indicated: all types, amounts of relays, ordering codes, proposed test switches and selector switches, applicable international standards to approve the functionality of proposed software and hardware |  |  |  |
| Estimated service life of proposed relay protection based on microprocessors |  |  |  |
| Additionally to the tender technical specifications, drawings of cubicles with equipment arrangement should be designed and submitted by the Tenderer |  |  |  |
| Relay protection and automation cubicles wiring tables should be designed and submitted by the Tenderer. Wiring tables shall include terminal column arrangement of relay protection cubicles with the following information: Marking of cable wire, information shall be fulfilled after project finalization; Terminal number in column; Project page number where terminal is used; Connection remote end address of wire. (in example: / 1L+20 / 3 / 5,15,30 / Q1-F501 /, which means, that circuit 1L+20 is connected to third terminal in column, circuit is located in pages 5, 15 and 30 of the given relay protection schemes, wire is connected to relay F501 terminal Q1) The Customer shall approve wiring tables |  |  |  |
| Relay protection cubicles shall be as follows: - Relay protection terminals shall be installed on front wall, front wall shall be with handle and open position fixation; - Backside montage plate for terminals and cable channels; - Plate for floor covering; - Bays shall be separated with left and right side plates; - Door switch, key shall be included; - Construction for outside cable fixation; - Terminals for earthing of cables and equipment; - For illumination of cubicles LED lamps should be used with luminous flux≥600lm; - Color RAL 7032; - Equipment shall be arranged as shown on Attachment “Cubicle layout”. - Note: In the Attachment general arrangement of relay protection equipment and devices is depictured. |  |  |  |
| 2 Customer’s engineers participation in the factory acceptance tests including travel, accommodation and meal expenses |  |  |  |
| Wiring of all cubicles should be marked. Marking shall indicate wire remote end address. |  |  |  |
| Current, voltage, trip, transfer commands and pick-up information terminals shall be interruptible. For current, voltage, trip, transfer commands and pick-up information terminals test sockets (plugs) for 4mm2 test wire connection shall be included. - For current, voltage, trip, transfer commands, pick-up, alarm, warning and circuit breaker information URTK/S terminals shall be used* - For disconnector position indication UK6N terminals shall be used* - All terminals shall be wired to the protection devices, spare wires shall be left at the equipment side. - Wiring bellow construction or fixation equipment, mounting rail is not allowed. *Other type of terminals shall be agreed by the Customer |  |  |  |
| All external tripping circuits, with are connected to binary inputs, shall be separated via auxiliary relays |  |  |  |
| Please indicate actual time for (Informative part): |  |  |  |
| relay protection cubicle designing works after project documentation receiving; | insert number of days |  |  |
| corrected wiring tables after commissioning; | insert number of days |  |  |
| SCS commissioning time after relay protection commissioning | insert number of days |  |  |
| Please indicate actual testing, check and commissioning time for bay: |  |  |  |
| 110kV line at substation: | insert number of days |  |  |
| busbars with bus coupler: | insert number of days |  |  |
| transformer: | insert number of days |  |  |
| repeated commissioning during reconstruction steps. | insert number of days |  |  |
| Note: In case of any discrepancies after ordering the Supplier is no way released from the obligation to perform entire commissioning without the Contract Price exchanges. |  |  |  |
| Proposed relay protection for each bay should be mounted and wired separately: |  |  |  |
| 110kV line protection at substation “Līvāni” - dimensions of cubicle; Following amount of main installation equipment shall be included: - 8 DC MCB’s, nominal current will be clarified during designing; - 80 URTK/S* terminals; - 300 UTME 4* terminals; - 100 UK6N* terminals; - 10 USLKGN 10N* terminals; - 20 PA1 – 4N plugs; - 15 auxiliary relays with base, 3NO/NC contacts, nominal power at least 3W like Finder 62.33.9.110.0300 with additional diode and resistance block; - 4 fast auxiliary relays with ≤ 8ms tripping time. Line differential protections and teleprotection relays for substation "Krustpils" and "Līksna" shall be installed in existing cubicles: Following amount of main installation equipment shall be included: - 2 DC MCB’s, nominal current will be clarified during designing; - 20 URTK/S* terminals; - 20 UTME 4* terminals; - 20 UK6N* terminals; - 5 USLKGN 10N* terminals; - 20 PA1 – 4N plugs; - 5 auxiliary relays with base, 3NO/NC contacts, nominal power at least 3W like Finder 62.33.9.110.0300 with additional diode and resistance block; - 2 fast auxiliary relays with ≤ 8ms tripping time. | in one cubicle 2200 x 900 x 600 mm (two cubicles at all) |  |  |
| 110kV busbar bay control module - dimensions of cubicle; Following amount of main installation equipment shall be included: - 4 DC MCB’s, nominal current will be clarified during designing; - 40 URTK/S* terminals; - 100 UTME 4* terminals; - 100 UK6N* terminals; - 10 USLKGN 10N* terminals; - 20 PA1 – 4N plugs; - 10 auxiliary relays with base, 3NO/NC contacts, nominal power at least 3W like Finder 62.33.9.110.0300 with additional diode and resistance block. - 2 fast auxiliary relays with ≤ 8ms tripping time. | in one cubicle 2200 x 900 x 600 mm |  |  |
| 110kV busbar and breaker failure protection Following amount of main installation equipment shall be included: - 40 DC MCB’s, nominal current will be clarified during designing; - 400 URTK/S* terminals; - 600 UTME 4* terminals; - 50 USLKGN 10N* terminals; - 200 PA1 – 4N plugs; - 50 auxiliary relays with base, 3NO/NC contacts, nominal power at least 3W like Finder 62.33.9.110.0300 with additional diode and resistance block; - 2 fast auxiliary relays with ≤ 8ms tripping time. | in separate cubicle(s) 2200 x 900 x 600 mm |  |  |
| Transformer protection - dimensions of cubicle; Following amount of main installation equipment shall be included: - 10 DC MCB’s, nominal current will be clarified during designing; - 80 URTK/S* terminals; - 200 UTME 4* terminals; - 100 UK6N* terminals; - 10 USLKGN 10N* terminals; - 20 PA1 – 4N plugs; - 50 auxiliary relays with base, 3NO/NC contacts, nominal power at least 3W like Finder 62.33.9.110.0300 with additional diode and resistance block; - 2 fast auxiliary relays with ≤ 8ms tripping time. | in two cubicles 2200 x 900 x 600 mm (four cubicles at all) |  |  |
| Transformer voltage regulation - dimensions of cubicle; - 10 DC MCB’s 2 pole, 2A; - 10 AC MCB’s 3 pole and C class, 4A; - 160 UTME 4* terminals; - 300 UK6N* terminals; - 60 PA1 – 4N plugs; - 100 USLKGN 10N* terminals. | in one cubicle 2200 x 900 x 600 mm |  |  |
| Anti static service kit like SPA-ZZ1 shall be delivered. |  |  |  |
| One set of wiring tools. If any specific wiring tools are not needed, then one set of screw drivers and crimping plier shall be delivered. |  |  |  |
| Delivered relay protection and automation should be entirely commissioned and co-operation of equipment checked by the Supplier. |  |  |  |
| The following scope of services for all delivered equipment and all substation bays where equipment will be located, excluding spare equipment are included in the Contract Price, including for line remote ends: |  |  |  |
| commissioning of relay protection, including cooperation test with existing relay protection equipment. Additionally made automation and protection functions shall be indicated and marked as tested. Information from setting list shall be used. Following amount of recommissioning shall be done: - after 1d step of reconstruction for one line; - after final step of reconstruction setting change for two lines, bus coupler and transformers. Re-commissioning shall be done in 30 days after receiving setting lists. |  |  |  |
| delivered protection shall be connected to SCS. |  |  |  |
| delivered line differential protections and teleprotection relays for substation "Krustpils" and "Līksna" shall be connected to existing SCS |  |  |  |
| testing of measuring transformers: current transformer and combined transformer current part polarity check; current transformer and combined transformer current part ratio check; current circuit resistance measurement; VA characteristic shall be given according to measured values for all current and combined transformer current part windings; current and voltage transformers, combined measurement transformers earthing check; |  |  |  |
| all secondary wiring check, including following: wiring of relay protection cubicle; wiring of external circuits from primary equipment wiring boxes till relay protection cubicles, including marshalling boxes; bay secondary part isolation measurement using 1kV; |  |  |  |
| the Commissioner shall check, that: relay protection devices can switch on / off circuit breakers, disconnectors and earthing switches; supplier shall test, that blocking scheme for disconnectors and earthing switches is working properly; permissible, blocking, switch on-to fault, including un-successful autorecloser cycle, and other mutual relay protection and automation functions cooperation between relay protection devices, which are mentioned in setting lists. |  |  |  |
| after energizing of the bay, the supplier shall check, that RP devices are measuring correctly. The supplier must be estimated that directional and differential protection are oriented correctly. |  |  |  |
| connection and commissioning of modems at substations and Relay department office |  |  |  |
| Ethernet modem (indicate) |  | 1 pc. |  |  |
| All necessary cables, junctions, couplers for modem connection (indicate) |  | yes |  |  |

The Supplier shall submit the following documentation to Relay Department of AST:

a) within 30 days after the ordering:

| Sets in digital form in the Latvian or English of the following manuals: |  |
| --- | --- |
| software manual; |  |
| application manual; |  |
| technical reference manual; |  |
| installation and commissioning manual; |  |
| operator’s manual; |  |
| manuals of relay protection units. |  |

b) right after commissioning and tests:

| Diagrams and settings in digital form. |  |
| --- | --- |
| 1 copy of corrected cubicle wiring tables |  |
| Protocols of performed tests and commissioning. The protocols should be written in the Latvian. Note: The takeover deed about the performed tests and commissioning will be signed by the Customer only after receipt of the protocols. Protocols shall include the following: Test set printouts (FREJA, OMICRON, ISA etc.) which indicate tested value and actual value in mentioned values (A, V, , 0, differential, biased etc) with actual feedback time and nominal reaction time. Relay parameter set. Relay configurations. |  |
| Commissioner shall provide Customer information about any change made in the relay protection and automation design. |  |

Relay protection shall be designed for:

| auxiliary voltage | 110V DC |  |
| --- | --- | --- |
| rated current | 1A |  |
| activation voltage of binary inputs by more than 50% and less than 80% of Urated | indicate |  |

The  numerical units mentioned in the Item 3.  shall also include the following:

| LCD display and navigation push buttons; |  |  |  |
| --- | --- | --- | --- |
| First optical interface for communication with the Substation control system (SCS). Use of the IEC 61850 communication protocol is requested. KEMA A level certificate or equal shall be provided. |  |  |
| Possibility of PC connection to the IEC61850 loop. All needed wires, switches and transducers shall be delivered |  |  |
| All needed optical wires (cables) shall be delivered, including one spare wire between relay protection device and Ethernet switches (two wires or cables at all) |  |  |
| Optical cables shall be used to connect devices outside the protection cubicles |  |  |
| Ethernet switches shall include the following: |  | See below |
| - Ordering code (Informative part) |  |  |
| - Quantity, including one spare Ethernet switch | 6 pcs |  |
| - Input and output memory for each port; |  |  |
| - Appropriate standard for use in electric power installations shall be delivered; |  |  |
| - Supporting of GOOSE (Generic Object Oriented Substation Event) telegrams; |  |  |
| - FEFI (Far Error Fault Indication) support; |  |  |
| - Network monitoring using SNMP (Simple Network Management Protocol); |  |  |
| - Supply voltage 110V DC (AC adapters can not be used); |  |  |
| - Customer’s made configuration of switch (with settable IP address etc.) ; |  |  |
| - Software for Customer’s made configuration shall be delivered; |  |  |
| - Ethernet switches shall be connected in the ring topology using redundancy protocol, for example RSTP (Rapid Spanning Tree Protocol); |  |  |
| - Broken loop shall be recognized in not less than 10ms; |  |  |
| Maintenance of separate relay protection device or Ethernet switch without disturbing rest of devices; |  |  |
| Freely configuration of information using IEC 61850 |  |  |
| Each supervision and failure indication to SCS shall be delayed for 10s; |  |  |  |
| During relay protection test all information to SCS shall be blocked via binary input or relay settings; |  |  |  |
| Second interface for connection to portable PC and communication software for: data exchange and parameterization of protection devices; readout and evaluation of fault reports and recorded disturbances; |  |  |  |
| Third interface for connection of those relays with disturbance recorder function. The communication software shall be provided to read-out fault data and recorded disturbances. |  |  |  |
| Built-in real time clock with resolution of 1 ms, with external time synchronization inputs and using IEC61850; |  |  |  |
| Service value reading (three phase current and voltage, active and reactive power, frequency, power factor, internal time etc.); |  |  |  |
| Continuous hardware and software self-supervision with fault indication (fault code); |  |  |  |
| Possibility to read-out and print all configurations and settings; |  |  |  |
| At least 10 programmable LED’s. LED indication for healthy state and internal fail state. After next pickup of protection device LED’s indication shall not be erased; |  |  |  |
| Supply voltage failures and relay restart cause not damage the information of events (trip, pickup and fault current) and oscillograms. |  |  |  |

1.1.  	110 kV lines

| Description: | Required: | Offered: |
| --- | --- | --- |
| Lines shall be protected and monitored with two separate numerical line differential and distance protection relays. |  |  |
| Differential, overcurrent and earth fault protections stages in all digital relays shall be with the following features: |  | See below |
| - Restriction during transformer inrush; |  |  |
| - Second harmonics restraint function with settable level the ratio of second harmonics to fundamental harmonics; |  |  |
| - Cross blocking between phases with second harmonic detection; |  |  |
| Voltage supply for line 110 kV circuit breaker shall be: separate DC voltage for the first tripping coil and for the second tripping coil + closing coil; separate auxiliary voltage MCB’s for each coil; |  |  |
| Two separate selector switches (one for each protection relay) for disconnecting of transmitted and received commands and signals to and from line remote- end (one NC, six NO contacts, 0,2 A, 110 V DC) shall be installed. |  |  |

1.1.1. Telesignaling devices.

| Description: | Required: |  | Offered: |
| --- | --- | --- | --- |
| Quantity | 5 pcs. |  |  |
| Ordering code |  |  |  |
| Telesignaling equipment shall be designed to transmit 16 commands and receive 16 commands. |  |  |  |
| Commands transmission time from binary input activation from transmitter to receiver binary output contact closing at line remote end ≤ 15 ms |  |  |  |
| Communication interface for multimode optical communication. Wires for connection to the communication equipment shall be included. |  | 4 pcs. |  |
| Communication interface for direct optical communication. Line length approx: LNr.296 47.9km; LNr.297 25.7km; Wires for connection to the communication equipment shall be included. |  | 4 pcs. |  |
| Ethernet communication interface |  |  |  |
| GOOSE signalling |  |  |  |
| Selector switches for disconnecting of transmitted and received commands from and to line remote-end (totally 16 NO contacts; 0,5 A; 220 V DC) shall be installed |  |  |  |
| Event recorder; |  |  |  |
| Trip value recorder; |  |  |  |
| Disturbance recorder with not less than 10 s of total recording time; |  |  |  |
| Extensive configuration possibilities by use of internal logical gates, timers and user configurable connection between different functions, binary inputs and outputs; |  |  |  |
| Binary inputs and groups | 16 |  |  |
| Binary NO outputs and groups | 16 |  |  |

1.1.2. Main protection at substation “Līvāni” LNr.296 and LNr.297.

| Description: | Required: |  | Offered: |  |
| --- | --- | --- | --- | --- |
| Quantity | 4 pcs |  |  |  |
| Spare line differential protection | 1 pc. |  |  |  |
| Single mode optical interface for direct communication. Line length approx: LNr.296 47.9km; LNr.297 25.7km. | 5 pcs. |  |  |  |
| Multi mode optical communication interface | 5 pcs. |  |  |  |
| Ordering code for line differential relay (Informative part) |  |  |  |  |
| Ordering code for optical communication interface (Informative part) |  |  |  |  |
| Ordering code for optical multi mode communication interface (Informative part) |  |  |  |  |
| Line current differential protection with both the current amplitude and phase angle measuring for each phase for two ends, with restrained and unrestrained differential protection stages, with differential current alarm with settable level |  |  |  |  |
| Parallel line compensation for fault locator |  |  |  |  |
| Transmission of information from 8 binary inputs via protection data interface. Information to binary inputs shall be provided via disconnectable terminals |  |  |  |  |
| Transfer trip function |  |  |  |  |
| Four-stage directional definite time overcurrent protection with freely selected directionality settings for each stage: “forward”, “reverse”, “non-directional” and with free selectable (configurable) of each stage as “On/Off”, “Switch on to fault protection”; |  |  |  |  |
| Any used overcurrent protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which overcurrent protection stage operates shall be sent to the control system. If the mentioned functionality is not possible, additional overcurrent protection stage shall be provided. |  |  |  |  |
| Any used overcurrent protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip, with voltage release from definite time undervoltage protection and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which overcurrent protection stage operates shall be sent to the SCS. If the mentioned functionality is not possible, additional overcurrent protection stage shall be provided. |  |  |  |  |
| Four - stage directional definite time earth fault protection with freely selected directionality settings for each stage: “forward”, “reverse”, “non-directional” and with free selectable (configurable) of each stage as “On/Off”, “Switch on to fault protection” |  |  |  |  |
| Any used earth fault protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which earth fault protection stage operates shall be sent to the SCS. If the mentioned functionality is not possible , additional protection stage shall be provided. |  |  |  |  |
| Three-phase tripping |  |  |  |  |
| Automatic (as separate function) or possibility to made by configuration switch-onto-fault logic operating at closing of circuit breaker manually and from autorecloser. If fault occurs within user set time after closing of circuit breaker, user freely selected protection stage must operate instantaneously |  |  |  |  |
| Fuse failure supervision function, which reacts on “3Uo without 3Io”; |  |  |  |  |
| Current circuit supervision |  |  |  |  |
| Fault locator, information shall be sent to SCS in metric units |  |  |  |  |
| Event recorder |  |  |  |  |
| Trip value recorder |  |  |  |  |
| Disturbance recorder with not less than 10 s of total recording time, with recording of all analogue channels |  |  |  |  |
| Four independent groups of setting parameters |  |  |  |  |
| Extensive configuration possibilities by use of internal logical gates, timers and user configurable connection between different functions, binary inputs and outputs |  |  |  |  |
| Shall be installed test switch (for tripping, closing, start of CBF, currents and voltage circuits disconnection during maintenance) without auxiliary relays) including test handle or plug |  |  |  |  |
| Ordering code for test switch (Informative part). |  |  |  |  |
| Analog current inputs for 110 kV side currents |  | 4 |  |  |
| Analog voltage inputs for 110 kV side line voltages |  | 3 |  |  |
| Analog voltage inputs for 110 kV side busbar voltage |  | 1 |  |  |
| Binary inputs and groups |  | 21 |  |  |
| Binary NO outputs and groups |  | 24 |  |  |

1.1.3. Back-up protection at substation “Līvāni” for lines LNr.296, LNr.297.

| Description: | Required: |  | Offered: |  |
| --- | --- | --- | --- | --- |
| Quantity | 2 pc. |  |  |  |
| Spare line distance protection | 1 pc. |  |  |  |
| Ordering code (Informative part) |  |  |  |  |
| Phase-to-phase and phase-to-ground distance protection with not less than six independently settable polygonal impedance measuring zones and freely settable directionality of not less than three zones |  |  |  |  |
| Possibility to cut the area of the load impedance out of the distance protection zones polygons with settable resistive reach and angle in forward and reverse directions |  |  |  |  |
| For each zone independently settable zero sequence reactance and resistance or earth return ratio |  |  |  |  |
| Parallel line compensation for fault locator and for distance protection at least for zone1 and zone 2; |  |  |  |  |
| Any distance protection zone shall provide functionality for instantaneous operation by acceleration command from the remote line end. Information about which distance protection zone operates shall be sent to the SCS. |  |  |  |  |
| Any used distance protection zone shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which distance protection zone operates shall be sent to the SCS. If the mentioned functionality is not possible, additional distance protection zone shall be provided. |  |  |  |  |
| Current reversal logic for distance protection and for earth fault protection; |  |  |  |  |
| Week infeed for distance protection and for earth fault protection; |  |  |  |  |
| Four stage directional overcurrent protection with freely selected directionality settings for each stage: “forward”, “reverse”, “non-directional” |  |  |  |  |
| Any used overcurrent protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which overcurrent protection stage operates shall be sent to the SCS. If the mentioned functionality is not possible, additional overcurrent protection stage shall be provided |  |  |  |  |
| Any used overcurrent protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip, with voltage release from definite time undervoltage protection and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which overcurrent protection stage operates shall be sent to the control system. If the mentioned functionality is not possible, additional overcurrent protection stage shall be provided. |  |  |  |  |
| Broken conductor protection; |  |  |  |  |
| Four stage directional earth fault protection with freely selected directionality settings for each stage: “forward”, “reverse”, “non-directional” |  |  |  |  |
| If relay uses the earth fault directional element for instantaneous operation by acceleration command from the remote line end, then additional 5th earth fault protection directional stage is not required. If relay uses earth fault protection directional stage for instantaneous operation by acceleration command from the remote line end, the relay shall have additional 5th earth fault protection directional stage which shall provide functionality. Information about which earth fault protection stage operates by the command from the remote line end shall be sent to the SCS. |  |  |  |  |
| Any used earth fault protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which earth fault protection stage operates shall be sent to the SCS. If the mentioned functionality is not possible, additional protection stage shall be provided. |  |  |  |  |
| Power swing detection with possibility to block user freely selected distance protection zones |  |  |  |  |
| Directional two stage over power protection. Each stage shall be with freely selected active, reactive or apparent power settings; |  |  |  |  |
| Directional two stage under power protection. Each stage shall be with freely selected active, reactive or apparent power settings; |  |  |  |  |
| Three phase two stage definite time undervoltage protection with freely selected phases / phase-to-phase voltages for each stage separately, with freely selected "OR / AND" logic for selected voltages for each stage separately; |  |  |  |  |
| Three phase two stage definite time overvoltage protection with freely selected phases / phase-to-phase voltages for each stage separately, with freely selected "OR / AND" logic for selected voltages for each stage separately; |  |  |  |  |
| Three-phase tripping; |  |  |  |  |
| Scheme communication logic for distance protection (permissive and blocking scheme); |  |  |  |  |
| Scheme communication logic for earth fault protection (permissive and blocking scheme); |  |  |  |  |
| Automatic or made by configuration switch-onto-fault logic operating at closing of circuit breaker manually and from autorecloser. If fault occurs within user set time after closing of circuit breaker, user freely selected distance protection zones, directional overcurrent and earth fault protection stages must operate instantaneously. |  |  |  |  |
| Fuse failure supervision function, which reacts on “3Uo without 3Io”; |  |  |  |  |
| Fuse failure supervision function, which reacts on “dU/dt without dI/dt”; |  |  |  |  |
| Current circuit supervision; |  |  |  |  |
| Four independent groups of setting parameters; |  |  |  |  |
| Fault locator, information shall be sent to SCS in metric units; |  |  |  |  |
| Event recorder; |  |  |  |  |
| Trip value recorder; |  |  |  |  |
| Disturbance recorder with not less than 10 s of total recording time, with recording of all analogue channels; |  |  |  |  |
| Extensive configuration possibilities by use of internal logical gates, timers and user configurable connection between different functions, binary inputs and outputs; |  |  |  |  |
| Setting group selection using the IEC 61850 communication protocol. |  |  |  |  |
| Shall be installed test switch (for tripping, closing, start of CBF, currents and voltage circuits disconnection during maintenance) without auxiliary relays) including test handle or plug; |  |  |  |  |
| Ordering code for test switch (Informative part). |  |  |  |  |
| Analog current inputs for 110 kV side currents |  | 4 |  |
| Analog voltage inputs for 110 kV side line voltages |  | 3 |  |
| Analog voltage inputs for 110 kV side busbar voltage |  | 1 |  |
| Binary inputs and groups |  | 21 |  |  |
| Binary NO outputs and groups |  | 24 |  |  |

1.2. 110kV lines and bus-coupler bay control modules at substation “Līvāni”.

| Description: | Required: |  | Offered: |  |
| --- | --- | --- | --- | --- |
| Bay control module shall be installed in the substation control room in protection cubicle of each particular bay according to single line diagram. | 3 pcs. |  |  |  |
| Spare bay control module (including auto-reclosing) | 1 pc. |  |  |  |
| Ordering code (Informative part) |  |  |  |  |
| Ordering code for trip circuit supervision relays |  |  |  |  |
| Local/Remote button or key to block control commands from control system |  |  |  |  |
| Three-phase auto-reclosing for 110kV lines circuit breakers with internal and external start and block (if not, then shall be delivered in separate unit) |  |  |  |  |
| Synchrocheck and voltage check for auto-reclosing of synchronous and asynchronous networks |  |  |  |  |
| Manual closing of circuit breaker of synchronous and asynchronous networks with separate from auto-reclosing synchrocheck and voltage check settings (if not, then shall be delivered in separate unit / please indicate it in “Offered”) |  |  |  |  |
| When manual closing is done should be indicated on local control PC and on SCADA measurements between synchronizing voltages: frequency difference (+/–), angle (+/–), voltages difference (+/–) |  |  |  |  |
| Four stage directional overcurrent protection with freely selected directionality settings for each stage: “forward”, “reverse”, “non-directional” |  |  |  |  |
| Four stage nondirectional overcurrent protection. |  |  |  |  |
| Any used overcurrent protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip, with voltage release from definite time undervoltage protection and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which overcurrent protection stage operates shall be sent to the SCS. If the mentioned functionality is not possible, additional overcurrent protection stage shall be provided. |  |  |  |  |
| Four stage directional earth fault protection with freely selected directionality settings for each stage: “forward”, “reverse”, “non-directional” |  |  |  |  |
| Four stage nondirectional earth fault protection. |  |  |  |  |
| Any used earth fault protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which earth fault protection stage operates shall be sent to the SCS. If the mentioned functionality is not possible , additional protection stage shall be provided. |  |  |  |  |
| Two stage non-directional definite time negative sequence overcurrent protection. |  |  |  |  |
| Automatic or made by configuration switch-onto-fault logic operating at closing of circuit breaker manually and from autorecloser. If fault occurs within user set time after closing of circuit breaker, user freely selected directional overcurrent and earth fault protection stages must operate instantaneously. |  |  |  |  |
| Thermal overload protection; |  |  |  |  |
| Broken conductor protection; |  |  |  |  |
| Directional two stage over power protection. Each stage shall be with freely selected active, reactive or apparent power settings; |  |  |  |  |
| Directional two stage under power protection. Each stage shall be with freely selected active, reactive or apparent power settings; |  |  |  |  |
| Three phase two stage definite time undervoltage protection with freely selected phases / phase-to-phase voltages for each stage separately, with freely selected "OR / AND" logic for selected voltages for each stage separately; |  |  |  |  |
| Three phase two stage definite time overvoltage protection with freely selected phases / phase-to-phase voltages for each stage separately, with freely selected "OR / AND" logic for selected voltages for each stage separately; |  |  |  |  |
| circuit breaker trip circuit supervision separately for both coils. For trip circuit supervision separate relays shall be used |  |  |  |  |
| On/off control of all controllable switching devices at the respective bay |  |  |  |  |
| User defined characteristic of maximum permissible number of interruptions as a function of the braking current. Circuit breaker resource in percents (0 – 100%) shall be indicated on LCD |  |  |  |  |
| LCD display showing the single line diagram of the bay and the real-time state of the switching devices. It shall be possible for the Purchaser to modify the single line diagram in case if the bay configuration is changed |  |  |  |  |
| Possibility to connect and configure using IEC 61850 protocol 10 binary inputs for connection to alarm system |  |  |  |  |
| Three-phase P, Q, U and I measurements with directionality determination, with two P >, Q >, U >, I > setpoints and two P <, Q <, U <, I < setpoints. Each setpoint shall be configurable with timers (settings not less than 100s) and logic elements. Measurement functions can be used; |  |  |  |  |
| Extensive configuration possibilities by use of internal logical gates, timers and user configurable connection between different functions, binary inputs and outputs |  |  |  |  |
| Four independent groups of setting parameters |  |  |  |  |
| Event recorder |  |  |  |  |
| Disturbance recorder with not less than 10 s of total recording time, with recording of all analogue channels |  |  |  |  |
| Analog current inputs for 110 kV side currents |  | 4 |  |  |
| Analog voltage inputs for three phase 110 kV side voltages |  | 3 |  |  |
| Analog voltage input for one phase 110 kV busbar voltage |  | 1 |  |  |
| Binary inputs |  | 55 |  |  |
| Binary inputs groups |  | 12 |  |  |
| Binary NO outputs |  | 35 |  |  |
| Binary output groups |  | 22 |  |  |
| Interlocking of the bays shall be done in bay control modules and including following functionality: |  |  |  |  |
| At least 8 separate outputs to block control function of disconnectors and earth switches with motor drive in the switchgear |  |  |  |  |
| At least 6 separate inputs to use state conditions from the other equipment of the substation |  |  |  |  |
| Interlocking logic shall be approved by the Customer |  |  |  |  |
| Setting group selection using the IEC 61850 communication protocol. |  |  |  |  |

1.3. 110 kV busbar protection and breaker failure protection.

| Description: | Required: |  |  | Offered: |
| --- | --- | --- | --- | --- |
| Quantity | 1 set |  |  |  |
| Ordering code (Informative part) |  |  |  |  |
| Breaker failure protection shall be implemented in busbar protection terminal or terminals; |  |  |  |  |
| Protection shall be low impedance numerical protection designed to trip separately each of the two busbars, with one extra bay (6 bays). Wiring shall be included; |  |  |  |  |
| Quantity of test plugs shall be equal to installed test switches |  | indicate |  |  |
| Ordering code for test switch and plug (Informative part) |  |  |  |  |
| Check zone; |  |  |  |  |
| End protection of bays; |  |  |  |  |
| Three-phase tripping; |  |  |  |  |
| Separate outputs for busbar protection trip; |  |  |  |  |
| Separate outputs of breaker failure protection re-trip and back-trip for each circuit-breaker |  |  |  |  |
| Automatic bay current measurement excluding from software in case if bay’s disconnector is opened; |  |  |  |  |
| Selector switch for switching on/off operation of busbar and circuit breaker protections; |  |  |  |  |
| Event recorder; |  |  |  |  |
| Disturbance recorder with not less than 5 s of recording time; |  |  |  |  |
| Shall be installed test handle for tripping and currents circuits disconnection during maintenance without auxiliary relays, including test switch or plug; |  |  |  |  |
| Busbar protection: |  |  |  |  |
| The busbar protection shall have check zone and shall be able to supervise isolators auxiliary contacts using the logic “Not CLOSED = OPENED”; |  |  |  |  |
| Stability for all external faults; |  |  |  |  |
| Detection of any external fault and CT saturation shall not affect the ability or time to detect an internal fault; |  |  |  |  |
| Function to cover the lacking protection of a part of the busbar due to CT arrangement; |  |  |  |  |
| Open current transformer’s circuit alarm; |  |  |  |  |
| Application with separate measuring for each phase; |  |  |  |  |
| Circuit-breaker failure protection: |  |  |  |  |
| Current check function for each phase; |  |  |  |  |
| Three-phase retrip and three-phase back-up trip; |  |  |  |  |
| To have accurate, consistent, short operate times and high overload capacity; |  |  |  |  |
| Transfer trip to faulty line remote end. |  |  |  |  |
| Binary inputs for each of 110 kV bays |  |  | 12 |  |
| Binary NO outputs for each of 110 kV bays and groups |  |  | 8 |  |

## 1.4.  Protection for power transformers TNr.1, TNr.2.

| Description: | Offered |
| --- | --- |
| Voltage supply for line 110 kV circuit breaker shall be: separate DC voltage for the first tripping coil and for the second tripping coil + closing coil; separate auxiliary voltage MCB’s for each coil |  |  |

## 1.4.1. Main protection for power transformers.

| Description: |  | Required: | Offered |
| --- | --- | --- | --- |
| Quantity |  | 2 pc. |  |
| One spare transformer differential relay |  | 1 pc. |  |
| Ordering code (Informative part) |  |  |  |
| Numerical transformer protections for power transformers: |  |  |  |
| Three-phase differential protection of three-winding power transformer with current compensation of ratio and phase, with zero sequence current elimination for three windings; |  |  |  |
| All built-in transformer’s protections shall be connected each to separate differential protection relay binary inputs and to bay control module using auxiliary relays. Note: please see 110kV circuit-breaker bay control relays; |  |  |  |
| Four stage nondirectional overcurrent protection for three windings. |  |  |  |
| Any used overcurrent protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which overcurrent protection stage operates shall be sent to the control system. If the mentioned functionality is not possible, additional overcurrent protection stage shall be provided. |  |  |  |
| Four stage nondirectional earth fault protection for three windings. |  |  |  |
| Any used earth fault protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which earth fault protection stage operates shall be sent to the control system. If the mentioned functionality is not possible , additional protection stage shall be provided. |  |  |  |
| Automatic or made by configuration switch-onto-fault logic operating at closing of 110 kV circuit breaker manually and from change-over. If fault occurs within user set time after closing of circuit breaker, user freely selected overcurrent and earth fault protection stages must operate instantaneously. |  |  |  |
| Low impedance restricted earth fault protections with current compensation of ratio for two windings; |  |  |  |
| Overexcitation protection for one winding; |  |  |  |
| Three phase two stage definite time undervoltage protection with phase-to-phase voltages measurement and "OR" operate logic; |  |  |  |
| Two stage negative sequence overcurrent protection for three windings; |  |  |  |
| Thermal overload protection for three windings; |  |  |  |
| Differential, restricted earth fault, overcurrent and earth fault protections stages shall be with the following features: |  |  |  |
| - Restriction during transformer inrush; |  |  |  |
| - Second harmonics restraint function with settable level the ratio of second harmonics to fundamental harmonics |  |  |  |
| - Differential protection shall be restrained during transformer overexcitation |  |  |  |
| - Fifth harmonics restraint function for differential protection |  |  |  |
| - Cross blocking between phases with second and fifth harmonics detection (both harmonics for differential protection and second harmonics for overcurrent and earth fault protections) |  |  |  |
| Programmable facility on binary inputs and outputs to provide trip, and / or indication of external protection units (Buchholz relay, temperature, oil level indicator etc.) |  |  |  |
| Event recorder; |  |  |  |
| Trip value recorder; |  |  |  |
| Disturbance recorder with not less than 10 s of total recording time, with recording of all analogue channels, including phases differential currents |  |  |  |
| Analog current inputs for 110 kV side currents | 3 |  |  |
| Analog current inputs for first medium voltage side currents | 3 |  |  |
| Analog current inputs for second medium voltage side currents | 3 |  |  |
| Analog current input for first neutral earthing transformer neutral current | 1 |  |  |
| Analog current input for second neutral earthing transformer neutral current | 1 |  |  |
| Analog voltage inputs for three phase voltages | 3 |  |  |
| Binary inputs and groups | 30 |  |  |
| Binary NO outputs and groups | 24 |  |  |
| Selector switch for gas protection for switching to trip/ signaling. |  |  |  |
| Setting group selection using the IEC 61850 communication protocol. |  |  |  |

## 1.4.2. Change-over of  Power transformers.

| Description: |  | Required: | Offered: |
| --- | --- | --- | --- |
| Quantity |  | 1 pc. |  |
| Ordering code (Informative part) |  |  |  |
| Freely configurable logic, which could be modified during commissioning: |  |  |  |
| Transformer protection initiates change over logic to close standby transformer circuit breakers immediately, including following verification: over and under voltage conditions (protections) which are described in transformer bay control modules; Transformer circuit breakers state (open/closed) shall be controlled. |  |  |  |
| Information about change over logic initiation shall be provided to medium voltage switchyard(s) |  |  |  |
| Change over cycle shall be blocked from external protection function (for example transformer overload protection); |  |  |  |
| Internal (virtual) logic position selector to switch on/off changeover from graphical display or SCS; |  |  |  |
| The logic shall not be affected by auxiliary supply lose or logic device restart; |  |  |  |
| After change-over cycle, the logic shall be switched to off; |  |  |  |
| Event recorder; |  |  |  |
| No analog current and voltage inputs | - |  |  |
| Binary inputs | 40 |  |  |
| Binary inputs groups | 12 |  |  |
| Binary NO outputs | 25 |  |  |
| Binary output groups | 12 |  |  |

## 1.4.3.   Voltage regulating equipment for tap-changer control of power transformers

Voltage regulating equipment for tap-changer control of 110/20/6 kV power transformers with the following features:

| Parameter | Required |  |  | Offered |
| --- | --- | --- | --- | --- |
| Quantity |  |  | 2 sets. |  |
| Ordering code (Informative part) |  |  |  |  |
| Voltage regulation | Line Drop Compensation (4 current sum) with time dependent U setpoint change (at least 24 setpoints) |  |  |  |
| Regulation mode (Automatic/Manual) controlled through binary input permanent | 1-Auto, 0-Manual |  |  |  |
| Tap changer’s Step# regulation for transformer in reserve | Tap changer’s step regulation automatically (predefined +/- step) for transformer in reserve (in accordance to step of a active transformer TC). |  |  |  |
| Voltage monitoring | Voltage asymmetry monitoring – blocking Voltage change after TC operation (<<) - blocking Undervoltage - High-speed switching Overvoltage - High-speed switching |  |  |  |
| Tap-changer drive monitoring and protection | Jammed Driver Driver Run Over (step by step - faulted) Command execution failure |  |  |  |
| Built-in real time clock | Resolution 1 sec |  |  |  |
| Visualization | The unit must indicate: Actual voltage, step, load, setpoint, regime. |  |  |  |
| Value recording | U, I, TC position 1/15 min (7 days) |  |  |  |
| Event recording | Alarms (with U, I, TC-pos.) 100 recordings |  |  |  |
| Extensive configuration | By use of internal logical gates, mathematical functions, timers and user configurable connection between different functions, binary inputs and outputs |  |  |  |
| Interface (for PC) | RS 485 / Ethernet |  |  |  |
| Power supply | External 100-220V AC/DC 10% 50Hz |  |  |  |
| Temperature limits | 0 +50C |  |  |  |
| Tap position measurement | Step # measurement input in regulator. Tap position must be read from potentiometer in tap change driver. Potentiometer impedance range are: 0-10Ω to 0-200Ω .One step impedance has to be freely changeable. Step# has to be converted to mA output (0-20mA) for measurement by “SCADA”. |  |  |  |
| Design | Panel mounting, modular type with separate display with size 6” |  |  |  |
| Analog current inputs IN = 1A or 5A |  | 6 |  |  |
| Analog voltage inputs UN = 100V AC |  | 6 |  |  |
| Binary inputs UN = 230V AC |  | 30 |  |  |
| Binary inputs groups |  | 5 |  |  |
| Binary outputs UN = 230V AC, breaking current 5A |  | 30 |  |  |
| Binary output groups |  | 10 |  |  |
| Analog output | (0-20mA), min quantity 1 freely changeable |  |  |  |
| Analog input | (0-20mA), min quantity 2 freely changeable |  |  |  |
| Measured values | U, I, P, Q, tap position |  |  |  |
| Voltage measurement accuracy | < 0,5% TRMS |  |  |  |
| Current measurement accuracy | < 0,5% TRMS |  |  |  |

## 1.4.4. 110kV circuit-breaker bay control modules

| Requested: |  |  | Offered |
| --- | --- | --- | --- |
| Bay control module shall be installed in the substation control room in protection cubicle of each particular bay according to single line diagram. | 2 pcs. |  |  |
| one spare bay control module | 1 pc |  |  |
| Ordering code |  |  |  |
| Ordering code for trip circuit supervision relays |  |  |  |
| Local/Remote button or key to block control commands from control system; |  |  |  |
| Four stage directional overcurrent protection with freely selected directionality settings for each stage: “forward”, “reverse”, “non-directional”;; |  |  |  |
| Four stage nondirectional overcurrent protection for three windings. |  |  |  |
| Any used overcurrent protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which overcurrent protection stage operates shall be sent to the SCS. If the mentioned functionality is not possible, additional overcurrent protection stage shall be provided. |  |  |  |
| Four stage directional earth fault protection with freely selected directionality settings for each stage: “forward”, “reverse”, “non-directional”;; |  |  |  |
| Four stage nondirectional earth fault protection for three windings. |  |  |  |
| Any used earth fault protection stage shall provide concurrent functionality for switch-onto-fault logic with instantaneous trip and freely selected blocking / not blocking from 2nd harmonic of the phase currents. Information about which earth fault protection stage operates shall be sent to the SCS. If the mentioned functionality is not possible , additional protection stage shall be provided. |  |  |  |
| One stage nondirectional overcurrent function for power transformer cooler starting; |  |  |  |
| Thermal overload protection for one winding; |  |  |  |
| Overcurrent and earth fault protections stages shall be with the following features: |  |  | See below |
| - Restriction during transformer inrush |  |  |  |
| - Second harmonics restraint function with settable level the ratio of second harmonics to fundamental harmonics |  |  |  |
| - Cross blocking between phases with second harmonic detection |  |  |  |
| Shall be possibly to start one stage of overcurrent protection from relay binary input (for undervoltage start from transformer medium or low voltage side); |  |  |  |
| Automatic or made by configuration switch-onto-fault logic operating at closing of 110 kV circuit breaker manually and from change-over. If fault occurs within user set time after closing of circuit breaker, user freely selected overcurrent and earth fault protection stages must operate instantaneously. |  |  |  |
| Minimal active power protection for 110 kV side with settable current (power) setting (minimal setting should be not bigger then 3 % from nominal current of relay) and with pickup time not bigger then 65 ms. If bay control module has not such function then can be used separate relay (static electronic or digital based relay). Mentioned function is foreseen for fast frequency load shedding stage blocking if substation is missed supply voltage from 110 kV network; |  |  |  |
| Three phase two stage definite time undervoltage protection with freely selected phases / phase-to-phase voltages for each stage separately, with freely selected "OR / AND" logic for selected voltages for each stage separately; |  |  |  |
| Undervoltage (one phase voltage measuring) protection for one phase analog voltage input for 110 kV busbar voltage with one stage and definite time operation only. The protection stage must be blocked if MCB for voltage transformer secondary wiring is opened. |  |  |  |
| Three phase two stage definite time overvoltage protection with freely selected phases / phase-to-phase voltages for each stage separately, with freely selected "OR / AND" logic for selected voltages for each stage separately; |  |  |  |
| Overvoltage (one phase voltage measuring) protection for one phase analog voltage input for 110 kV busbar voltage with one stage and definite time operation only. Should be separate binary output from this protection. |  |  |  |
| Voltage control for change over logic: if transformer, which is in operation, voltage on 110 kV side is lost for more than 0 s - 10 s and voltage on opposite 110 kV busbars exists, then this transformer shall be tripped and change over cycle shall be initiated. These logic should be automatically switch on if 110 kV section disconnector is opened and should be automatically blocked if booth section disconnectors are closed; |  |  |  |
| For stage overfrequency/underfrequency with freely selected settings for each stage: “overfrequency”, “underfrequency”. |  |  |  |
| Rate of change of frequency (ROCOF) protection. |  |  |  |
| Circuit breaker trip circuit supervision separately for both coils. For trip circuit supervision separate relays shall be used |  |  |  |
| On/off control of all controllable switching devices at the respective bay; |  |  |  |
| User defined characteristic of maximum permissible number of interruptions as a function of the braking current. Circuit breaker resource in percent’s (0 – 100%) shall be indicated on LCD; |  |  |  |
| LCD display showing the single line diagram of the bay and the real-time state of the switching devices. It shall be possible for the Purchaser to modify the single line diagram in case if the bay configuration is changed; |  |  |  |
| Possibility to connect and configure using IEC61850 protocol 10 binary inputs for connection to alarm system; |  |  |  |
| Extensive configuration possibilities by use of internal logical gates, timers and user configurable connection between different functions, binary inputs and outputs and I, U, P, Q of the bay; |  |  |  |
| Event recorder |  |  |  |
| Disturbance recorder with not less than 10 s of total recording time, with recording of all analogue channels |  |  |  |
| Analog current inputs for 110 kV side currents |  | 4 |  |
| Analog voltage inputs for three phase 110 kV side voltages |  | 3 |  |
| Analog voltage input for one phase 110 kV busbar voltage |  | 1 |  |
| Binary inputs |  | 55 |  |
| Binary inputs groups |  | 12 |  |
| Binary NO outputs |  | 35 |  |
| Binary output groups |  | 22 |  |
| All built-in transformer’s protections shall be connected to four binary inputs of transformer 110kV circuit-breaker bay control module: to first binary input gas protections which trip transformer; to second binary input transformer gas protections which operate to alarm, to third binary input all protections in parallel which trip transformer, to fourth binary input all other protections in parallel which operate to alarm. Note: please see transformer differential relay; |  |  |  |
| Interlocking of the bays shall be done in bay control modules and including following functionality: |  |  |  |
| at least 8 separate outputs to block control function of disconnectors and earth switches with motor drive in the switchgear; |  |  |  |
| at least 6 separate inputs to use state conditions from the other equipment of the substation; |  |  |  |
| interlocking logic shall be approved by the Customer. |  |  |  |
| Setting group selection using the IEC 61850 communication protocol. |  |  |  |

1.5. Training for delivered relay protection equipment.

| Description |  | See below |
| --- | --- | --- |
| Following training for 2 engineers in the factory intelligence center or laboratory should be included in the Contract Price, including travel, accommodation and meal expenses: |  |  |
| - Days for training | Please indicate |  |
| - Name of intelligence center | Please indicate |  |
| - Line distance protection |  |  |
| - Line differential protection |  |  |
| - Busbar and breaker protection |  |  |
| - Transformer differential protection |  |  |
| - Relay protection with IEC61850 |  |  |
| The training should be finished at least one month before commissioning works on site. |  |  |
| The training should be performed on the equipment and software provided for delivery or identical |  |  |
| After the successful training it should be acknowledged with issuance of appropriate certificate to the trained personnel |  |  |