Annex 11

Procurement ID No AST2024/91

Joint Stock Company "Augstsprieguma tīkls"

open procedure

"Supply of electrical equipment to the 110 kV substation "Līvāni""

(ID No AST2024/91)

Lot 3 "110 kV Metering units"

Technical specification, technical offer (updated 30.10.2024.)

Tenderer  _______

General Requirements

| Description: | Required: | Offered: |
| --- | --- | --- |
| Requirements for all equipment: | See below |  |
| Each type of the offered equipment shall be type tested and passed routine tests before delivery | yes |  |
| Standards applicable to the type and routine tests | IEC / CENELEC |  |
| The type test reports shall be available to the Purchaser | yes |  |
| Technical proposal should be prepared according to attached single line diagram | yes |  |
| All instrument transformers must have the same type of insulation - either gas or liquid. Instrument transformers with different types of insulation must not be offered | yes |  |
| Single-line diagram of the substation see in above | noted | noted |

## 1. 110 kV combined metering units

| Description: | Required: | Offered: |
| --- | --- | --- |
| Type of design: gas or paper/liquid insulated | yes/please specify |  |
| Measuring transformer hermetically sealed | yes |  |
| Combined metering units (item 1.2) shall be accompanied with valid certificate of Latvian National Metrology Centre at the time of delivery | yes |  |
| Current transformer part | See below |  |
| Item 1.1 quantity (lines) | 6 phases |  |
| 1-st core accuracy class | 0,5S FS 5 |  |
| Rated primary current / secondary current | 600-1200 / 1 A |  |
| Rated output | 5 VA |  |
| 2-nd core accuracy class | 5 P 30 |  |
| Rated primary current / secondary current | 600-1200 / 1 A |  |
| Rated output | 20 VA |  |
| 3-rd core accuracy class | 5 P 30 |  |
| Rated primary current / secondary current | 600-1200 / 1 A |  |
| Rated output | 20 VA |  |
| 4-th core accuracy class | 5 P 30 |  |
| Rated primary current / secondary current | 600-1200 / 1 A |  |
| Rated output | 20 VA |  |
| Approximately Ri for 5P30 windings | Please specify in Ω |  |
| Primary current setting changeable in primary part | yes |  |
| Item 1.2 quantity (transformers) | 6 phases |  |
| 1-st core accuracy class | 0,5 S FS 5 |  |
| Rated primary current / secondary current | 50-100 / 1A |  |
| Rated output | 10 VA |  |
| 2-nd core accuracy class | 5 P 30 |  |
| Rated primary current / secondary current | 300 / 1A |  |
| Rated output | 20 VA |  |
| 3-rd core accuracy class | 5 P 30 |  |
| Rated primary current / secondary current | 300 / 1A |  |
| Rated output | 20 VA |  |
| 4-th core accuracy class | 5 P 30 |  |
| Rated primary current / secondary current | 300 / 1A |  |
| Rated output | 20 VA |  |
| Approximately Ri for 5P30 windings | Please specify in Ω |  |
| Primary current setting changeable in secondary part | yes |  |
| #### Voltage transformer part | See below |  |
| Item 1.1. quantity (lines) | 6 phases |  |
| Transformer ratio | 11030,130,13kV |  |
| 1-st secondary measuring winding accuracy class | 0,5 |  |
| Rated output | 10 VA |  |
| 2-nd tertiary earth-fault winding accuracy class | 3 P |  |
| Rated output | 10 VA |  |
| Rated continuous voltage factor | 1,2 Un |  |
| 30 sec voltage factor | 1,5 Un |  |
| Item 1.2. quantity (transformers) | 6 phases |  |
| Transformer ratio | 11030,130,13kV |  |
| 1-st secondary measuring winding accuracy class | 0,5 |  |
| Rated output | 10 VA |  |
| 2-nd tertiary earth-fault winding accuracy class | 3 P |  |
| Rated output | 10 VA |  |
| Rated continuous voltage factor | 1,2 Un |  |
| 30 sec voltage factor | 1,5 Un |  |
| Requirements for gas insulated measuring transformer | See below |  |
| Insulation medium: eco-efficient gas (GWP=0) | yes |  |
| Insulation medium type | please specify |  |
| Eco-efficient gas density monitor with two step signalling | yes |  |
| Eco-efficient gas density monitor with MPa/bar scale | yes |  |
| Eco-efficient gas leakage rate | ≤ 0,5% p.y. |  |
| Eco-efficient gas for the first filling included | yes |  |
| Temperature-compensated pressure reading with MPa/bar scale | yes |  |
| Overpressure relief device (rupture disc) | yes |  |
| External thread for eco-efficient gas filling equipment connection | please specify |  |
| Requirements for paper/liquid insulated measuring transformer | See below |  |
| Insulation medium: synthetic ester or biodegrable oil | yes/please specify |  |
| Insulation medium type | please specify |  |
| Fluid level indicator | yes |  |
| Leakproof design | yes |  |
| Tested by leak detection | yes |  |
| Stainless steel expansion bellows for fluid | yes |  |
| Synthetic ester according IEC 61099 | yes |  |
| Biodegrable oil according IEC 60296 | yes |  |
| Common requirements | See below |  |
| Composite insulators with silicone sheds | yes |  |
| Rated short-time withstand current (3 s) | ≥ 20 kA |  |
| Rated peak withstand current | ≥ 50 kA |  |
| Rated voltage | ≥ 123 kV |  |
| Rated power frequency withstand voltage | ≥ 230 kV |  |
| Rated lightning impulse withstand voltage | ≥ 550 kV |  |
| Insulation requirements of secondary terminals | ≥ 3 kV |  |
| Interturn insulation requirements | ≥ 4,5 kV |  |
| Rated frequency | 50 Hz |  |
| Creepage distance (phase - ground) | ≥ 43,3 mm / kV |  |
| Ambient air temperature range | -40°C up to +40°C |  |
| Intended for out-door installation | yes |  |
| Standards | IEC 61869-1, 61869-4 |  |
| Rated continuous thermal current factor | 1,2 In |  |
| Distance between hole centres of terminals | 45 45 mm |  |
| Terminals for control, earthing and shield | yes |  |
| Feed – through secondary terminal blocks (e.g. Phoenix UT 10) | yes/please specify |  |
| All steel parts – hot-dip galvanised or of stainless steel | yes |  |
| Marking of all internal wiring should be made | yes |  |
| End of VT primary winding (terminal N) should be in terminal box | yes |  |
| Terminal box of non-corroding cast aluminium or stainless steel with air vent | yes |  |
| Secondary cable gland plate undrilled, at the bottom of terminal box | yes |  |
| Degree of protection for terminal box | ≥ IP-54 |  |
| Scheme plate | yes |  |
| To the tender should be attached operating, maintenance and installation manuals in Latvian or English and preliminary drawing of offered equipment | yes |  |
| All nameplates in Latvian | yes |  |
| Informative part: | See below |  |
| Manufacturer | please indicate |  |
| Type No. | please specify type No. |  |
| Internal arc fault protection class (Class IA1 or Class IA2) | please specify |  |
| Static withstand load | kN |  |
| Max thermal burden | VA |  |
| Eco-efficient gas nominal pressure at 20°C | MPa/bar |  |
| Quantity of eco-efficient gas or insulated liquid for 1 phase | kg |  |
| Approx. total weight of 1 phase-unit | kg |  |

1.3. Special tools and services

| Equipment for gas filling (only for gas insulated instrument transformers) | 1 set |  |
| --- | --- | --- |
| Eco-efficient gas pressure gauge with necessary o-rings for it exchange (only for gas insulated instrument transformers) | 3 units |  |
| Oil sampling equipment (only for paper/liquid insulated instrument transformer) | 1 set |  |
| For each liquid insulated instrument transformer liquid DGA should be performed after instrument transformer routine test | yes |  |

## 2. 110 kV voltage transformers

| Description: | ##### Required: | ##### Offered: |
| --- | --- | --- |
| Type of design: inductive, gas or paper/liquid insulated | Yes/please specify |  |
| Measuring transformer hermetically sealed | yes |  |
| Quantity | 2 phases |  |
| Transformer ratio | 11030,130,13kV |  |
| Rated continuous voltage factor | 1,2 Un |  |
| 30 sec voltage factor | 1,5 Un |  |
| 1-st secondary measuring winding accuracy class | 0,5 |  |
| Rated output | 20 VA |  |
| 2-nd tertiary earth-fault winding accuracy class | 3 P |  |
| Rated output | 20 VA |  |
| Requirements for gas insulated measuring transformer | See below |  |
| Insulation medium: eco-efficient gas (GWP=0) | yes |  |
| Insulation medium type | please specify |  |
| Eco-efficient gas density monitor with two step signalling | yes |  |
| Eco-efficient gas density monitor with MPa/bar scale | yes |  |
| Eco-efficient gas leakage rate | ≤ 0,5% p.y. |  |
| Eco-efficient gas for the first filling included | yes |  |
| Temperature-compensated pressure reading with MPa/bar scale | yes |  |
| Overpressure relief device (rupture disc) | yes |  |
| External thread for eco-efficient gas filling equipment connection | please specify |  |
| Requirements for paper/liquid insulated measuring transformer | See below |  |
| Insulation medium: synthetic ester or biodegrable oil | yes/please specify |  |
| Insulation medium type | please specify |  |
| Fluid level indicator | yes |  |
| Leakproof design | yes |  |
| Tested by leak detection | yes |  |
| Stainless steel expansion bellows for fluid | yes |  |
| Synthetic ester according IEC 61099 | yes |  |
| Biodegrable oil according IEC 60296 | yes |  |
| Common requirements | See below |  |
| Composite insulators with silicone sheds | yes |  |
| Rated voltage | ≥ 123 kV |  |
| Rated power frequency withstand voltage | ≥ 230 kV |  |
| Rated lightning impulse withstand voltage | ≥ 550 kV |  |
| Insulation requirements of secondary terminals | ≥ 3 kV |  |
| Interturn insulation requirements | ≥ 4,5 kV |  |
| Rated frequency | 50 Hz |  |
| Creepage distance (phase - ground) | ≥ 43,3 mm / kV |  |
| Ambient air temperature range | -40°C up to +40°C |  |
| Intended for out-door installation | yes |  |
| Standards | IEC 61869-1 IEC 61869-3 |  |
| Distance between hole centres of terminals | 45 45 mm |  |
| Terminals for control, earthing and shield | yes |  |
| Feed – through secondary terminal blocks (e.g. Phoenix UT 10) | yes/please specify |  |
| All steel parts – hot-dip galvanised or of stainless steel | yes |  |
| Marking of all internal wiring should be made | yes |  |
| End of VT primary winding (terminal N) should be in terminal box | yes |  |
| Terminal box of non-corroding cast aluminium or stainless steel with air vent | yes |  |
| Secondary cable gland plate undrilled, at the bottom of terminal box | yes |  |
| Degree of protection for terminal box | ≥ IP-54 |  |
| Scheme plate | yes |  |
| To the tender should be attached operating, maintenance and installation manuals in Latvian or English and preliminary drawing of offered equipment (only in electronic format) | yes |  |
| All nameplates in Latvian | yes |  |
| Informative part: | See below |  |
| Manufacturer | please indicate |  |
| Type No. | please specify type No. |  |
| Internal arc fault protection class (Class IA1 or Class IA2) | please specify |  |
| Static withstand load | kN |  |
| Max thermal burden | VA |  |
| Eco-efficient gas nominal pressure at 20°C | MPa/bar |  |
| Quantity of eco-efficient gas or insulated liquid for 1 phase | kg |  |
| Approx. total weight of 1 phase-unit | kg |  |

2.1. Special tools and services

| Eco-efficient gas pressure gauge with necessary o-rings for it exchange (only for gas insulated instrument transformers) | 1 unit |  |
| --- | --- | --- |
| For each liquid insulated instrument transformer liquid DGA should be performed after instrument transformer routine test | yes |  |

## 3. Technical documentation and services for all primary equipment

| Description: | Required: | Offered: |
| --- | --- | --- |
| Primary equipment Operations, Maintenance and Installation manuals in Latvian and English. | In electronical PDF file format by e-mail. Not later than two months before delivery of equipment |  |
| Preliminary outline drawings, details of the required foundations, assembly drawings, detailed specifications of all connecting interfaces and secondary wiring and terminals diagrams. | In electronical PDF format by e-mail. Within 60 days after signing of Contract |  |
| Technical data sheet according IEC standard. | In electronical PDF format by e-mail Within 60 days after signing of Contract |  |
| The corrected outline drawings, details of the required foundations, assembly drawings, detailed specifications of all connecting interfaces and secondary wiring and terminals. | In electronical PDF and DWG formats by e-mail. Within 14 days after Purchaser’s approval diagrams |  |
| DGA test reports (only for oil insulated instrument transformers) and routine test protocols | In electronic PDF file format by e-mail. |  |