Annex 9

Procurement ID No AST2024/91

Joint Stock Company "Augstsprieguma tīkls"

open procedure

"Supply of electrical equipment to the 110 kV substation "Līvāni""

(ID No AST2024/91)

Lot 2 "110 kV Circuit-breakers"

Technical specification, technical offer (updated 30.10.2024.)

Tenderer  _______

General Requirements

| Description: | Required: | Offered: |
| --- | --- | --- |
| Each type of the offered equipment shall be type tested and passed routine tests before delivery | yes |  |
| Standards applicable to the type and routine tests | IEC / CENELEC |  |
| The type test reports shall be available to the Purchaser | yes |  |
| Technical proposal should be prepared according to attached single line diagram | yes |  |

1. 110 kV eco-efficient gas circuit-breaker

| Description: | Required: | Offered: |
| --- | --- | --- |
| Quantity | 4 units |  |
| Rated normal current | ≥ 1600 A |  |
| Rated short-circuit breaking current | ≥ 20 kA |  |
| Rated short-time withstand current (3 s) | ≥ 20 kA |  |
| Rated short-circuit making current | ≥ 50 kA |  |
| Rated peak withstand current | ≥ 50 kA |  |
| Rated voltage | ≥ 123 kV |  |
| Rated frequency | 50 Hz |  |
| Rated power frequency withstand voltage to earth and between phases | ≥ 230 kV |  |
| Rated power frequency withstand voltage across open pole | ≥ 230 kV |  |
| Rated lightning impulse withstand level (LIWL) to earth and between phases | ≥ 550 kV |  |
| Rated lightning impulse withstand level (LIWL) across open pole | ≥ 550 kV |  |
| Rated out-of-phase breaking current (out-of-phase voltage factor) | ≥ 5 kA (2,0 p.u.) |  |
| Rated line-charging breaking current (at a voltage range factor) | ≥ 31,5A (1,2 p.u.) |  |
| Rated cable-charging breaking current (at a voltage range factor) | ≥ 140A (1,2 p.u.) |  |
| Creepage distance (phase - ground) | ≥ 43,3 mm / kV |  |
| First-pole-to-clear factor | 1,3 |  |
| Number of interrupting units | 1 |  |
| Ambient air temperature range | -40°C up to +40°C |  |
| Intended for out-door installation | yes |  |
| Mechanical endurance class | M1 or M2 |  |
| Dead time | 300ms |  |
| Interruption medium (eco-efficient gas or vacuum) | please indicate |  |
| Eco-efficient gas density monitor with two step signalling connected through self-closing valve | yes |  |
| Eco-efficient gas density monitor with MPa/bar scale | yes |  |
| Eco-efficient gas leakage rate | ≤0.5% y |  |
| Eco-efficient gas for the first filling included | yes |  |
| Flat primary terminals with 4 drillholes positioned in square | yes |  |
| Distance between hole centres of terminals | 45 45 mm |  |
| Composite or porcelain insulator | yes/please specify |  |
| Without steel supporting structures | yes |  |
| Pole columns mounted on hot-dip galvanised base frame | yes |  |
| Spring operating mechanism for three-pole operating | yes |  |
| Control voltage for motor, closing and tripping coils | 110 V DC |  |
| Auxiliary voltage for heating of operating mechanisms | 230/400 V AC |  |
| Number of closing coils | 1 |  |
| Number of tripping coils | 2 |  |
| Rated operating sequence | O-0,3s-CO-15s-CO |  |
| Motor protection by MCB | yes |  |
| Operating mechanism with limit switch for emergency hand operation | yes |  |
| Operating cycle counter (none-resettable) | yes |  |
| Pushbuttons or switch “on/off” for operation on-site | yes |  |
| Selector switch “local/remote/off” for control variations | yes |  |
| Lettering on pushbuttons and switches should be in Latvian language | yes |  |
| Electrical local-remote control | yes |  |
| Contacts for electrical interlocking | yes |  |
| Terminals for control, motor circuit, earthing and shield | yes |  |
| Disconnectable secondary terminal blocks (e.g. Phoenix URTK) | yes/please specify |  |
| Free auxiliary contacts | ≥ 10 NO, ≥ 10 NC, 1 W |  |
| Marking of all internal wiring in operating mechanism should be made | yes |  |
| Operating mechanism boxes mounted to the steel structure under the pole | yes |  |
| Operating mechanisms situated in lockable non-corroding cast aluminium or stainless steel boxes with air vent | yes/please specify |  |
| Degree of protection for terminal and operating mechanism boxes | ≥ IP-54 |  |
| Door locking with butterfly nut and possibility for padlock | yes |  |
| Operating mechanism boxes with panel light and 230V socket outlet (CEE 7/7) | yes |  |
| With necessary crank handles | yes |  |
| To the tender should be attached operating, maintenance and installation manuals in Latvian or English and preliminary drawing of offered equipment | yes |  |
| Standard | IEC 62271-100 |  |
| All nameplates in Latvian | yes |  |
| Informative part: | See below |  |
| Manufacturer: | please indicate |  |
| Type | please specify type |  |
| Opening time | ms |  |
| Rated brake time | ms |  |
| Arcing time | ms |  |
| Closing time | ms |  |
| Simultaneity difference between poles (on / off) | ms |  |
| Rated mechanical terminal load (stat.+dyn.) | kN |  |
| Quantity of Eco-efficient gas for 1 phase-unit | kg |  |
| Eco-efficient gas nominal pressure at 20°C | MPa/bar |  |
| Approx. total weight of 1 phase-unit | kg |  |
| Power consumption per closing coil | W |  |
| Power consumption per tripping coil | W |  |
| Charging time of closing spring | s |  |
| Power consumption per motor | W |  |
| Anti-condensation heating via thermal relay (if applicable) | W |  |
| Anti-condensation permanent heating | W |  |

1.1. Spare parts and special tools

| Electric drive motor | 1 unit |  |
| --- | --- | --- |
| Tripping and closing coils of each type | 1 set |  |
| Heating element | 3 units |  |
| Auxiliary relays of each type | 1 set |  |
| Operation counter | 1 unit |  |
| Necessary lubricants for installing procedure | yes |  |
| Eco-efficient gas pressure gauge with necessary o-rings for it exchange | 1 unit |  |

1.2. Services, testing and commissioning

| Filling of Eco-efficient gas, testing and commissioning of installed circuit-breakers. | 2 times in Latvia |  |
| --- | --- | --- |
| Training of two customer employees about circuit breaker installation, commissioning and maintenance in the training center of circuit breaker manufacturer | 1 set |  |

## 2. Technical documentation and services for all primary equipment

| Description: | Required: | Offered: |
| --- | --- | --- |
| Primary equipment Operations, Maintenance and Installation manuals in Latvian and English. | In electronical PDF file format by e-mail. Not later than two months before delivery of equipment |  |
| Preliminary outline drawings, details of the required foundations, assembly drawings, detailed specifications of all connecting interfaces and secondary wiring and terminals diagrams. | In electronical PDF format by e-mail. Within 60 days after signing of Contract |  |
| Technical data sheet according IEC standard. | In electronical PDF format by e-mail Within 60 days after signing of Contract |  |
| The corrected outline drawings, details of the required foundations, assembly drawings, detailed specifications of all connecting interfaces and secondary wiring and terminals. | In electronical PDF and DWG formats by e-mail. Within 14 days after Purchaser’s approval diagrams |  |