Annex 7

Procurement ID No AST2024/91

Joint Stock Company "Augstsprieguma tīkls"

open procedure

"Supply of electrical equipment to the 110 kV substation "Līvāni""

(ID No AST2024/91)

Lot 1 "110 kV Disconnectors"

Technical specification, technical offer (updated 30.10.2024.)

Tenderer

General Requirements

| Description: | Required: | Offered: |
| --- | --- | --- |
| Requirements for all equipment: | See below |  |
| Each type of the offered equipment shall be type tested and passed routine tests before delivery | yes |  |
| Standards applicable to the type and routine tests | IEC / CENELEC |  |
| The type test reports shall be available to the Purchaser | yes |  |
| Technical proposal should be prepared according to attached single line diagram | yes |  |

## 1. 110 kV horizontal centre-break disconnectors

| Description: | ##### Required: | ##### Offered: |
| --- | --- | --- |
| Item 1.1. Horizontal centre-break motor driven disconnector without earthing switch | 2 units |  |
| Item 1.2. Horizontal centre-break motor driven disconnector with motor driven earthing switch on one side | 6 units |  |
| Rated normal current | ≥ 1600A |  |
| Rated short-time withstand current (3 s) | ≥ 20 kA |  |
| Rated peak withstand current | ≥ 50 kA |  |
| Rated voltage | ≥ 123kV |  |
| Rated frequency | 50 Hz |  |
| Rated power frequency withstand voltage to earth and between phases | ≥ 230 kV |  |
| Rated power frequency withstand voltage across isolating distance | ≥ 265 kV |  |
| Rated lightning impulse withstand voltage to earth and between phases | ≥ 550 kV |  |
| Rated lightning impulse withstand voltage across isolating distance | ≥ 630 kV |  |
| Creepage distance (phase - ground) | ≥ 43,3 mm / kV |  |
| Ambient air temperature range | -40°C up to +40°C |  |
| Intended for out-door installation | yes |  |
| Mechanical endurance class for disconnectors | M1 |  |
| Electrical endurance class for earthing switches | E0 |  |
| Flat primary terminals with 4 drillholes positioned in square | yes |  |
| Distance between hole centres of terminals | 45 45 mm |  |
| Main contacts made of copper, with a silver-plated surface | yes |  |
| Porcelain insulator and flange juncture covered with silicone layer | yes |  |
| Porcelain insulators should be manufactured in European union | yes |  |
| Base rotary unit should be with two bearings inside | yes |  |
| Linkages between phases should be with spherical bearings on ends | yes |  |
| Current path contact (rotary) heads made from one piece of cast aluminium alloy | yes |  |
| Earthing switch contact arms (pipes) should be painted or glued with red and white adhesive film in five bands (white/red/white/red/white). | yes |  |
| Without steel supporting structures | yes |  |
| Pole columns with insulators should be mounted at the factory on hot-dip galvanised base frame including all supporting elements | yes |  |
| Mechanical and electrical interlocking between disconnector and earthing switch. Mechanical locking must be realized at open position of disconnector and motor drive must be switched off. Whenever the crank is inserted in the drive mechanism, it shall be impossible to operate the device electrically. | yes |  |
| With dead-centre interlock | yes |  |
| One operating mechanism for three pole operating | yes |  |
| Control voltage for motor | 110 V DC |  |
| Auxiliary voltage for heating of operating mechanisms | 230/400 V AC |  |
| Motor protection by MCB | yes |  |
| Operating mechanism with limit switch for emergency hand operation | yes |  |
| Pushbuttons or switch “on/off” for operation on-site | yes |  |
| Selector switch “local/remote/off” for control variations | yes |  |
| Lettering on pushbuttons and switches should be in Latvian language | yes |  |
| Electrical local-remote control | yes |  |
| Terminals for control and motor circuit, earthing and shield | yes |  |
| Disconnectable secondary terminal blocks (e.g. Phoenix URTK) | yes/please specify |  |
| Free auxiliary contacts | ≥ 10 NO, ≥ 10 NC, 1 W |  |
| Contacts for electrical interlocking | yes |  |
| Marking of all internal wiring in operating mechanism should be made | yes |  |
| Operating mechanisms lowered down, fixed to the steel structure | yes |  |
| Operating mechanisms for disconnector and earthing switch should be located under side pole | yes |  |
| Operating mechanism for disconnector should be located at opposite side of main contacts opening direction | yes |  |
| Operating mechanisms situated in lockable non-corroding cast aluminium or stainless steel boxes with air vent | yes/please specify |  |
| Secondary cable gland plate undrilled, at the bottom of operating mechanism box | yes |  |
| Degree of protection for terminal and operating mechanism boxes | ≥ IP-54 |  |
| Door locking with butterfly nut and possibility for padlock | yes |  |
| With necessary crank handles | yes |  |
| To the tender should be attached operating, maintenance and installation manuals in Latvian or English and preliminary drawing of offered equipment (only in electronic format) | yes |  |
| Standard | IEC 62271-102 |  |
| All nameplates in Latvian | yes |  |
| Informative part: | See below |  |
| Manufacturer | please indicate |  |
| Type No. Item 1.1 | please specify |  |
| Type No. Item 1.2 | please specify |  |
| Straight load | kN |  |
| Cross load | kN |  |
| Approx. total weight of 1 unit | kg |  |
| Anti-condensation heating via thermal relay (if applicable) | W |  |
| Anti-condensation permanent heating | W |  |

### 1.3. Spare parts for 110 kV disconnectors

| Description: | Required: | Offered: |
| --- | --- | --- |
| Electric drive motor of each type | 1 unit |  |
| Heating element | 3 units |  |
| Main contacts for disconnector | 1 set |  |
| Main contacts for earthing switch | 1 set |  |
| Electrical interlocking coil and contacts | 1 set |  |
| Necessary lubricants for installing procedure | yes |  |

## 2.Single-column 72,5 kV earthing switches

| Description: | ##### Required: | Offered: |
| --- | --- | --- |
| Knife type single-column earthing switches, motor driven | 2 units |  |
| Earthing switch provided for power transformer neutral point grounding | yes |  |
| Rated short-time withstand current (1 s) | ≥ 20 kA |  |
| Rated peak withstand current | ≥ 50 kA |  |
| Rated voltage | 72,5kV |  |
| Rated frequency | 50 Hz |  |
| Rated power frequency withstand voltage to earth and between phases | ≥ 140 kV |  |
| Rated power frequency withstand voltage across isolating distance | ≥ 325 kV |  |
| Creepage distance (phase - ground) | ≥ 43,3 mm / kV |  |
| Ambient air temperature range | -40°C up to +40°C |  |
| Intended for out-door installation | yes |  |
| Electrical endurance class | E0 |  |
| Flat primary terminals with 4 drillholes positioned in square | yes |  |
| Distance between hole centres of terminals | 45 45 mm |  |
| Porcelain insulator and flange juncture covered with silicone layer | yes |  |
| Porcelain insulators should be manufactured in European union | yes |  |
| Earthing switch contact arms (pipes) should be painted or glued with red and white adhesive film in three bands (red/white/red). | yes |  |
| Without steel supporting structures | yes |  |
| Earthing switch should be mounted at the factory on hot-dip galvanised base frame including all supporting elements | yes |  |
| With dead-centre interlock | yes |  |
| Control voltage for motor | 110 V DC |  |
| Auxiliary voltage for heating of operating mechanisms | 230/400 V AC |  |
| Motor protection by MCB | yes |  |
| Operating mechanism with limit switch for emergency hand operation | yes |  |
| Pushbuttons or switch “on/off” for operation on-site | yes |  |
| Selector switch “local/remote/off” for control variations | yes |  |
| Lettering on pushbuttons and switches should be in Latvian language | yes |  |
| Electrical local-remote control | yes |  |
| Terminals for control and motor circuit, earthing and shield | yes |  |
| Disconnectable secondary terminal blocks (e.g. Phoenix URTK) | yes/please specify |  |
| Free auxiliary contacts | ≥ 10 NO, ≥ 10 NC, 1 W |  |
| Marking of all internal wiring in operating mechanism should be made | yes |  |
| Operating mechanisms lowered down, fixed to the steel structure | yes |  |
| Operating mechanisms situated in lockable non-corroding cast aluminium or stainless steel boxes with air vent | Yes/please specify |  |
| Degree of protection for terminal and operating mechanism boxes | ≥ IP-54 |  |
| Door locking with butterfly nut and possibility for padlock | yes |  |
| With necessary crank handles | yes |  |
| To the tender should be attached operating, maintenance and installation manuals in Latvian or English and preliminary drawing of offered equipment | yes |  |
| Standard | IEC 62271-102 |  |
| All nameplates in Latvian | yes |  |
| Informative part: | See below |  |
| Manufacturer | please indicate |  |
| Type | please specify |  |
| Straight load | kN |  |
| Cross load | kN |  |
| Approx. Total weight of 1 unit | kg |  |
| Anti-condensation heating via thermal relay (if applicable) | W |  |
| Anti-condensation permanent heating | W |  |

### 2.1. Spare parts for 72,5 kV earthing switches

| Description: | Required: | Offered: |
| --- | --- | --- |
| Electric drive motor of each type | 1 unit |  |
| Heating element | 1 unit |  |
| Main contacts for earthing switch | 1 set |  |
| Electrical interlocking coil and contacts | 1 set |  |
| Necessary lubricants for installing procedure | yes |  |

## 3. Technical documentation and services for all primary equipment

| Description: | Required: | Offered: |
| --- | --- | --- |
| Primary equipment Operations, Maintenance and Installation manuals in Latvian and English. | In electronical PDF file format by e-mail. Not later than two months before delivery of equipment |  |
| Preliminary outline drawings, details of the required foundations, assembly drawings, detailed specifications of all connecting interfaces and secondary wiring and terminals diagrams. | In electronical PDF format by e-mail. Within 60 days after signing of Contract |  |
| Technical data sheet according IEC standard. | In electronical PDF format by e-mail Within 60 days after signing of Contract |  |
| The corrected outline drawings, details of the required foundations, assembly drawings, detailed specifications of all connecting interfaces and secondary wiring and terminals. | In electronical PDF and DWG formats by e-mail. Within 14 days after Purchaser’s approval diagrams |  |