7. pielikums

Iepirkuma ID Nr. AST2026/81

nolikumam

| Akciju sabiedrība "Augstsprieguma tīkls" atklāta sarunu procedūra "Releju aizsardzības un automātikas pārbaudes iekārtu piegāde" (ID Nr. AST2026/81) Tehniskā specifikācija | JSC "Augstsprieguma tīkls" open negotiation procedure "Supply of Relay Protection and Automation Test Equipment" (ID No AST2026/81) Technical specification |
| --- | --- |

Technical specification for Supply of Relay Protection and Automation Test Equipment

- Relay test set

| Description: |  | Required: | Proposed: |
| --- | --- | --- | --- |
| Portable test set |  | 2 set |  |
| Ordering code |  | indicate |  |
| Hardware: |  |  |  |
| Analog output channel |  | At least 7 total outputs simultaneously (accepts convertible voltage/current channels) |  |
| Voltage output channels |  | At least 4 (dedicated or convertible channels) |  |
| Voltage range |  | 0 ÷ 300V |  |
| Accuracy |  | ≤ 0.1% amplitude error, ≤ 0.1° phase error |  |
| Power |  | ≥ 75VA |  |
| Frequency range |  | 0 ÷ 1000Hz |  |
| Current output channels |  | At least 6 (dedicated or convertible channels |  |
| Current range for one current output |  | 0 ÷ 30A |  |
| Accuracy |  | ≤ 0.1% amplitude error, ≤ 0.1° phase error |  |
| Power |  | ≥ 150VA |  |
| Frequency range |  | 0 ÷ 1000Hz |  |
| Maximum current for test set |  | indicate |  |
| Binary inputs convertible (voltage/contact) preferably each galvanically isolated |  | ≥ 10 |  |
| Binary outputs Breaking capacity |  | ≥ 4 AC: P ≥ 2000VA at 300V DC: P ≥ 50W at 300V |  |
| DC voltage output Power |  | 12 ÷ 250V DC ≥ 50W (continuous) |  |
| Communication interfaces |  |  |  |
| IEC 61850 Support (GOOSE, Sampled values) |  |  |  |
| Weight including accessories (indicate) | ≤ 20 kg |  |  |
| Operating Temperature |  |  |  |
| Storage temperature |  |  |  |
| Power supply |  |  |  |
| Software: |  |  |  |
| Software (indicate) |  |  |  |
| Software for testing modules: - Overcurrent protection test; - Line distance protection test , it shall be possible to see fault values for selected test points. Testing shall be done using: (shot test; search test; Check test (checking of distance protection zone at defined error)); - Transformer differential protection test, using transformer parameters. External and internal fault simulation; - Sequences of analogue and digital generation. Sequence shall be continued (not stopped) also if conditions are obtained. It shall be possible to see fault values for test points; - Change of current and voltage values as ramp or step mode, increasing or decreasing amplitude, angle or frequency at the same time - Harmonics distortion test. |  |  |  |
| Relay manufacturer templates and RIO and XRIO (relay setting visualization) type files (Alstom, GE, Siemens, Hitachi, ABB etc.) |  |  |  |
| COMTRADE (existing fault files from disturbance recorder) format files playback |  |  |  |
| Ability to create complex multi-step test sequences (end-to-end logic and protection testing) in one file |  |  |  |
| Configurable, auto-generated test reports (PDF, DOC, Excel, with logos, signatures, etc.) |  |  |  |
| Software set for IEC 61850 |  |  |  |
| Testing software for testing, troubleshooting, commissioning and IED development, test set mapping and configuration with the GOOSE messages on the substation network |  |  |  |
| Test module for sampled values generation, sampled values shall be visible (RMS and phase angles) |  |  |  |
| Sampled values simultaneous streams (publishing) | At least 2 |  |  |
| Cyber Security |  |  |  |
| Secure Firmware Update | Digitally signed firmware packages |  |  |
| Communication Encryption | Encrypted communication |  |  |
| Accessories: |  |  |  |
| Soft travel case |  |  |  |
| Warranty: |  |  |  |
| Warranty at least 36 months (indicate) |  |  |  |
| Certifications & Compliance: |  |  |  |
| CE certified |  |  |  |
| ISO 9001 manufacturing standard |  |  |  |

- Current transformer (CT) test set

Current transformer (CT) test set may be either a standalone unit or a part/function of a relay test set

| Description: |  | Required: | Proposed: |
| --- | --- | --- | --- |
| Portable test set |  | 2 set or 2 parts/functions for relay test set |  |
| Ordering code |  | indicate |  |
| Hardware: |  |  |  |
| Current transformer (CT) test tool (the device may be either a standalone unit or a part/function of a digital relay testing device) |  |  |  |
| Software for testing: - CT polarity test; - CT ratio test - CT secondary winding resistance test; - CT knee point; - CT burden test; - CT demagnetization function. |  |  |  |
| Weight including accessories (indicate) | ≤ 20 kg |  |  |
| Operating Temperature |  |  |  |
| Storage temperature |  |  |  |
| Power supply |  |  |  |
| Accessories: |  |  |  |
| Wires and other accessories required for CT tests (clamps, terminal adapter, etc) |  |  |  |
| Soft travel case |  |  |  |
| Warranty |  |  |  |
| Warranty at least 36 months (indicate) |  |  |  |
| Certifications & Compliance: |  |  |  |
| CE certified |  |  |  |
| ISO 9001 manufacturing standard |  |  |  |