Annex 6

To the Procurement ID No. RS2026/104/AK

Regulations

Date of update: 29.06.2026

TECHNICAL SPECIFICATION

Construction and Replacement of the 115/10.5 kV Transformer TNo.1

Construction plan: “Development of the construction plan and design supervision for the replacement of the 115/10.5 kV transformer TNo.1 and the 10.5 kV relay protection.”

Object: Heating Plant “Imanta”, Kurzemes prospekts 17, Riga, LV-1067

Customer: JSC RĪGAS SILTUMS

Designer: SIA RKF SEDL

- Description of the current situation

The Heating Plant (hereinafter – the “HP”) “Imanta”, located at Kurzemes prospekts 17, Riga, was constructed in 1974 on the left bank of the Daugava River. The HP “Imanta” is the largest heat source of JSC RĪGAS SILTUMS and operates within the integrated heating networks on the left bank of the Daugava River. The total installed electricity generating capacity of the HP “Imanta” is 47.7 MW, while the permitted consumption load is 40 MW. JSC RĪGAS SILTUMS has installed an electrode water heating boiler with a capacity of 50 MW (hereinafter – the “EL WHB”) at the HP “Imanta” to generate thermal energy using electricity when electricity prices on the exchange are low, as well as to use the EL WHB to participate in the provision of reserve services to the transmission system operator. At this time, the EL WHB is operating at a limited load of 35 MW, the boiler’s maximum capacity is limited by the rated capacity of transformer TNo.1, which is 40 MVA. Following the replacement and installation of transformer TNo. 1, an increase in the permitted consumption load of the HP “Imanta” to 53.5 MW is planned, as well as operation of the EL WHB at its rated capacity.

- General requirements

  - The Contractor shall carry out the replacement of the 110 kV transformer TNo. 1 and the related works at the HP “Imanta” in accordance with the approved construction plan “Development of the construction plan and design supervision for the replacement of the 115/10.5 kV transformer TNo.1 and the 10.5 kV relay protection” (hereinafter – the “Works”).

  - In accordance with the construction plan, at this stage the replacement of three protection relays on the 110 kV side, L610 protection relays, and the related communications / telecommunications part shall be carried out. In order to submit a correct financial offer, it is necessary to familiarise oneself with the construction plan, and it is recommended to visit the object.

  - The Contractor shall include in its offer a detailed Work Performance Schedule for the HP “Imanta”, separately specifying:

    - the transformer manufacturing period at the manufacturer’s factory;

    - the transformer delivery period (including transportation) to the object.

  - The Contractor shall provide the Customer with a weekly report on the Works completed in accordance with the accepted Work Performance Schedule.

  - Prior to starting the Works, the Contractor shall fully familiarise itself with all construction plan documentation (drawings, specifications, explanatory description, calculations).

  - The installation of the new transformer on the foundations and its assembly shall be carried out by the transformer supplier.

  - Before starting Work, develop a work execution plan (hereinafter – the “WEP”) and coordinate it with the Customer, which shall include technical solutions, labour protection measures, the sequence of installation, and preparatory measures for the work.

  - The materials specified in the Technical Specification may be replaced with equivalent quality and design products of other manufacturers only upon coordination with the author of the Construction Plan.

  - High-quality materials complying with the specifications of the Construction Design shall be used in the performance of the Works.

  - All works shall be carried out in accordance with the applicable Latvian Construction Standards (LBN), Cabinet Regulations, LVS EN and LEK standards.

  - The materials specification may not include all materials indicated in the drawings. When preparing the construction works estimate, the Contractor shall also include materials indicated in the drawings and Construction Plan documentation but not included in the materials specification, as well as auxiliary materials for dismantling (spill absorbents, oil containers, lifting equipment, etc.).

  - Prior to dismantling, the Contractor shall, together with the Customer, prepare the technical condition deed of the existing transformer (oil volume, damage, insulation resistance prior to disconnection).

  - The Contractor shall provide photographic documentation before start of the Works, during the Works and after replacement of the transformer.

- Technical specifications of the transformer

| No. | Description | Parameter | Notes |
| --- | --- | --- | --- |
| 1 | Installation method | Outdoor installation |  |
| 2 | Type | Oil-immersed transformer |  |
| 3 | Number of phases | 3 |  |
| 4 | Power | 63 MVA |  |
| 5 | Rated frequency | 50 Hz |  |
| 6 | Primary voltage | 115 kV |  |
| 7 | Secondary voltage | 10.5 kV |  |
| 8 | Final group | YNd11 |  |
| 9 | Primary-side voltage regulator | ±4x2.5% |  |
| 10 | Voltage regulator type | Manual (voltage-free switch-over) |  |
| 11 | Cooling system | ONAF Oil Natural Air Force |  |
| 12 | Work cycle | C |  |
| 13 | Maximum ambient temperature | 40°C |  |
| 14 | Noise level | ≤ 70 dB(A) in accordance with EN 60076-10 |  |
| 15 | Earth terminal |  |  |
| 16 | Wheels on the chassis with flanges |  | The current track gauge is 1530 mm. |

  - The transformer must comply with the following standards:

- EN 60076-1:2011 “Power Transformers – General Requirements”

- IEC 60076-5:2006 “Power Transformers – Short Circuit Withstand Capability”

- EN 60076-10 -10:2016 “Power Transformers – Determination of Sound Levels”

- LVS EN Standards (Standards currently in force in the Republic of Latvia).

  - Transformer windings must ensure thermal stability during short circuit conditions in accordance with IEC 60076-5:2006. The short circuit endurance of all windings must be at least 3 seconds at all voltage levels of the windings. Annex 3 to the Technical Specification – technical data for the manufacturer’s 63MVA transformer “FABRYKA Transformatorow w Zychlinie Sp. z o.o. Catalogue data sheet TOc 63000/115F”. The contractor may propose an alternative transformer if its technical specifications meet the requirements of the Construction Plan and its dimensions can be adapted to the existing foundation.

- Integral current transformer on the 110 kV side

  - Current transformer specifications

For Phase U:

| Designation | Transformation ratio | Power | Class of accuracy | Note |
| --- | --- | --- | --- | --- |
| T1 | 400/1 A | 30 VA | 0.5 cl. FS10 |  |
| T2 | 1000/1 A | 30 VA | 5P cl. ALF20 |  |
| T3 | 1000/1 A | 30 VA | 5P cl. ALF20 |  |
| T4 | 1000/1 A | 30 VA | 5P cl. ALF20 |  |

For Phase V:

| Designation | Transformation ratio | Power | Class of accuracy | Note |
| --- | --- | --- | --- | --- |
| T1 | 400/1 A | 30 VA | 0.5 cl. FS10 |  |
| T2 | 1000/1 A | 30 VA | 5P cl. ALF20 |  |
| T3 | 1000/1 A | 30 VA | 5P cl. ALF20 |  |
| T4 | 1000/1 A | 30 VA | 5P cl. ALF20 |  |
| T5 | 400/1 A | 15 VA | 3 cl. FS10 | for coil temperature control |

For Phase W:

| Designation | Transformation ratio | Power | Class of accuracy | Note |
| --- | --- | --- | --- | --- |
| T1 | 400/1 A | 30 VA | 0.5 cl. FS10 |  |
| T2 | 1000/1 A | 30 VA | 5P cl. ALF20 |  |
| T3 | 1000/1 A | 30 VA | 5P cl. ALF20 |  |
| T4 | 1000/1 A | 30 VA | 5P cl. ALF20 |  |

  - A principle scheme of the current transformer connections is provided in the Construction Plan.

- Minimum transformer configuration:

- Manual voltage regulator ±4x2.5%;

- Buchholz gas relay;

- Flow switch;

- Magnetic oil level gauge;

- 2-contact thermometer (for oil temperature);

- 2-contact thermometer (for coil temperature);

- Thermometer;

- Resistance-type temperature sensor;

- Resistance-type thermometer with digital display;

- Automatic cooling system with ARI from two power sources;

- Working voltage of control and signalling circuits: 220 VDC;

- Self-diagnostics of the cooling system faults;

- *Additional condition: If the power consumption of the cooling system exceeds 25 kW, amendments to the Construction Plan shall be made (to be coordinated with the Customer and the designer);

- Automatic anti-condensation heating of the transformer control and monitoring distribution panel;

- Moisture absorber;

- Safety valve;

- Built-in transformers on the 110 kV side in accordance with the Construction Plan;

- When ordering a transformer, provision must be made for the installation of brackets for mounting electric-surge arresters. The bracket drawing is provided in the Construction Plan.

- Construction and installation works

  - General works:

    - preparation and arrangement of the construction site;

    - if necessary, restoration of the road surface or fencing damaged during the relocation of the transformer;

    - after completion of all Works, the territory of the HP “Imanta” within the boundaries of the work area shall be restored to proper order.

  - Dismantling works (dismantling of the old transformer TNo. 1)

    - Elements to be retained (dismantle and hand over to the Customer):

      - flexible busbars AC 300 – disconnect from the existing TNo. 1 transformer. Dismantle the existing AC 300 flexible busbars and replace them with new busbars of the required length;

      - electric-surge arresters – dismantle 3EL2 096-2PJ31-4NAO and 3EL2 048-2SF31-4NAO, retain for future use;

      - 10.5 kV power supply cables of the electric boiler (18 pcs.) – disconnect from the busbar bridge, retain for future use;

      - transformer oil – drain and retain for future use.

    - Dismantling sequence (mandatory):

      - disconnect the flexible busbars AC 300 from the transformer;

      - disconnect the connection on the 10.5 kV side from the existing busbar bridge;

      - disconnect the 10.5 kV power supply cables of the electric boiler;

      - disconnect the earth busbar;

      - disconnect and dismantle the secondary circuit cables (control, signalling);

      - drain the oil from the transformer tank and oil conservator (retain for future use).

      - after draining the oil, seal the transformer outlet pipes with oil-resistant covers;

      - dismantle the oil coolers (before moving the transformer);

      - high-voltage bushings – do not dismantle (leave on the transformer);

      - disconnect the old TNo. 1 transformer and dismantle it from the foundations;

      - prepare a temporary storage (preservation) area in accordance with the Construction Plan;

      - move the transformer to the temporary storage (preservation) area;

      - place and leave the old TNo. 1 transformer in a fully assembled condition, the transformer shall be positioned so that it does not obstruct the delivery and installation of the new transformer.

    - Restrictions

      - moving the transformer with the oil coolers installed is not permitted;

      - the coolers may only be moved after the oil has been drained and the pipes have been sealed.

    - Waste management

      - all waste generated during dismantling (oily materials, scrap metal, asbestos-containing gaskets, if any) shall be sorted and disposed of in accordance with the laws and regulations of the Republic of Latvia.

    - Installation and commissioning of the new transformer

      - check the compliance of the existing foundations with the dimensions and loads of the new transformer;

      - installation of the new transformer on the foundations – precise positioning using the current track (gauge 1530 mm);

      - connection of the neutral terminal of the new 63MVA transformer to the electric-surge arrester;

      - the enclosure of the new 110kV transformer shall be earthed at two points. Earthing shall be connected to the existing earth system at the HP “Imanta”;

      - if necessary, the newly installed transformer shall be levelled on the foundations so that the inclination of the tank towards the conservator is approximately 1–1.5 degrees;

      - connection on the 110 kV and 10.5 kV sides (in accordance with the Construction Plan). Connect the new flexible 110kV AC300 busbars to the new TNo. 1 transformer. Use new fastening elements;

      - connection of the cooling system in accordance with the scheme in the Construction Plan;

      - connection of secondary circuits (Buchholz relay, thermometers, level sensors, cooling control, etc.);

      - filling of oil to the specified level, taking an oil sample for analysis;

      - vacuum drying before oil filling (residual pressure ≤ 1 mbar).

    - Installation of new secondary cables

Due to the replacement of the transformer, the following new secondary circuit cables shall be installed:

| Cable designation | Application |
| --- | --- |
| D02.11 | Transformer differential protection current circuits |
| D02.29 | Transformer equipment status signal cable |
| CHL10W2000 | Maximum current protection circuits for the KL610 cable lines |
| CHL10W2001 | Differential protection current circuits for the KL610 cable lines |
| 0BHF2001, 0BHF2002 | Power supply of the transformer cooling system and the automatic anti-condensation heating of the switchgear |

Notes:

The cable types to be used, their lengths and connection points are specified in:

- cable connection schemes;

- cable log;

- connection scheme.

Cable end processing, conductor connection, and marking must be performed in accordance with the requirements of the laws and regulations of the Republic of Latvia.

    - Relay protection and control requirements

      - install the relay protection (RPA) circuits for the new transformer TNo. 1 and line LN610 with new relays (differential protection relay, MSA current protection relay, and transformer protection relay);

      - install new secondary cable sections from the transformer to the RPA panels. If necessary, provide for the installation of additional control cables;

      - connect the transformer differential protection;

      - connect the transformer fault warning system;

      - connect the current circuits of the new TNo. 1 current transformers to the 10BBD02 RPA circuits;

      - in the CHL10 panel, connect the differential protection and MSA current circuits of the line KL610;

      - connect the current circuits of the new TNo. 1 current transformers and the voltage circuits of the voltage transformers to the LNo. 610 and TNo. 1 RPA circuits, and test their secondary circuits. If the instrument transformers are supplied by the Contractor, the Contractor shall ensure that the tests specified in the technical specification are carried out after installation of the instrument transformers and installation of the secondary cables;

      - dismantle unused RA equipment and cables;

      - processing the ends of control cables for new transformers, inspecting, connecting, and marking the wires;

      - carry out the necessary modifications for connecting the RPA equipment to the existing dispatch control system and the new AVS/SCADA solution, ensuring the correct transmission, display, testing and documentation of all telesignalling, telemetering, alarm, event and control signals provided for in the project.

    - Installation of the partial discharge monitoring system. General requirements:

      - The Construction Design has been developed based on the equipment offer and technical data of the OMICRON manufacturer;

      - installation of specialised diagnostic systems manufactured by the OMICRON company intended for different types of equipment:

| Equipment | DI monitoring system |
| --- | --- |
| Cable lines | OMICRON MONCABLO |
| Generators (2 units) | OMICRON MONGEMO |
| Transformers (2 units) | OMICRON MONTESTO |

      - DI monitoring system data processing shall be carried out from one common server, by installing a shared server with software;

      - ensure power supply to the DI equipment in accordance with the Construction Plan;

      - locate the DI monitoring system with sensors in accordance with the Construction Plan;

      - carry out installation and final assembly on site based on the manufacturer’s documentation;

      - cooperation with the equipment manufacturer (OMICRON) is recommended for the installation and commissioning of the DI monitoring systems;

      - after installation of the DI monitoring system, perform system operation testing and calibration;

      - document the test results in a protocol and submit it to the Customer;

      - provide personnel training for work with the DI monitoring system.

    - Scope of works for the DMS section

      - reconstruction of the existing 110kV dispatch control system in accordance with the developed Construction Plan;

      - purchase and installation of additional equipment and materials provided for in the Construction Plan;

      - dismantling of the old DMS control cables;

      - testing and adjustment;

      - within the scope of the Construction Design, ensure the integration of transformer TNo. 1, 10.5 kV RPA, DMS and the related technological signals of the HP “Imanta” into a unified control / SCADA solution. The new solution shall be compatible with JSC RĪGAS SILTUMS long-term SCADA maintenance approach, providing for the use of Siemens WinCC 8.x or Siemens WinCC OA SCADA software. The selected solution shall be agreed with the Customer prior to implementation;

      - the AVS/RTU / controller solution shall ensure secure data acquisition from RPA equipment, transformer control devices, cooling control, DI monitoring and other project-related nodes. IEC 61850, IEC 60870-5-104 and / or OPC UA shall be provided as the primary data exchange protocols. Modbus TCP/RTU or discrete / analogue I/O signals shall only be permitted where the equipment does not support the above protocols or where technically justified;

      - The existing Arcus Elektronika automation distribution system and the associated signals, control, indication, warning, emergency, and interlock functions shall be inspected and recorded in a signal list prior to dismantling. All signals and functions necessary for operation shall be transferred to the new AVS/SCADA solution. The existing distribution system may only be dismantled after successful signal transfer, functional testing and approval by the Customer;

      - the Contractor shall develop and agree with the Customer a complete signal list, which shall at least specify: signal ID/KKS, name, type, unit of measurement, source, protocol / address, update frequency, alarm limits, priority, SCADA display and transmission to AST, where applicable;

      - the SCADA solution shall provide at least: display of current measurements and statuses, recording of alarms and events, auditing of user actions, archiving of historical data for essential measurements, operator screens for displaying transformer TNo. 1 and all related RPA/DMS equipment and monitoring of the related systems;

      - prior to commissioning, FAT/SAT or equivalent tests shall be carried out, verifying all signals from the source to SCADA, correctness of alarms, control / interlocking functions, communication loss scenarios and data archiving. The tests shall be documented in protocols. The system shall be deemed acceptable only after all critical and material non-conformities have been remedied;

      - the executable documentation shall additionally include the up-to-date signal list, AVS/SCADA architecture scheme, network connection scheme, configuration backups, SCADA project files, licence information, description of users and access rights, operating instructions and administrator’s instructions.

    - Testing and adjustment

      - ensure the installation of primary and secondary equipment in accordance with the equipment installation and adjustment instructions, document the results in protocols and submit them to the Customer;

      - for the works performed and tests carried out, in accordance with the laws and regulations of the Republic of Latvia and the requirements of JSC RĪGAS SILTUMS, the following executable documentation shall be submitted:

- acceptance deeds for significant structures regarding the installation of metal structures, with annexes The annexes shall include declarations of the performance characteristics of the materials used, as well as the calibration certificate of the torque wrench used for tightening the bolts;

- declarations of the performance characteristics for all construction products used;

- concealed works deeds for the installation of reinforced concrete foundations, installation of the earth system, laying of cables and / or their protective conduits, with annexes. The annexes shall include declarations of the performance characteristics of the materials used;

- installation deeds with annexes for the installation of all equipment, terminal boxes, cable glands, etc. The annexes shall include declarations of performance characteristics or technical data sheets of the installed equipment;

- factory test protocols for the supplied equipment;

- factory service instructions and dimensional drawings for the supplied equipment.

      - the Contractor shall perform the following measurements and submit the measurement protocols. The calibration certificate of the measuring instruments used shall be attached to the protocol annexes:

- measurements of contact resistance of the contact points of bolted electrical connections of 10kV electrical installations;

- measurements of the earth system (continuity of the circuit) of equipment, structures, terminal boxes, etc.;

- transformer insulation resistance measurements;

- transformer winding direct current resistance measurements;

- transformer transformation ratio test;

- full oil analysis (before switching on);

- insulation resistance measurements of 0.4kV power and secondary cables;

- 10kV cable insulation measurement;

- 10kV busbar bridge insulation measurement;

- testing of RPA circuits (current, voltage, control, signalling);

- testing of cable connections from the primary equipment cabinet to the protection relay;

- testing of circuit continuity and correctness of connections (including inspection of terminal box installation);

- testing of the direct current resistance and insulation of current circuits;

- testing of signal circuit connections;

- testing of control and trip circuit connections;

- testing of earth system of current and voltage circuits;

- perform tests of the correctness of connections of DMS telesignalling, telemetering and telecontrol circuits;

- testing of the cooling system automation;

- testing of the operation of the Buchholz relay, flow relay and thermometers.

    - Basic requirements for the installation and marking of secondary cables and their conductors

      - Procedure for distribution blocks:

          - distribution blocks located outdoors shall be made of stainless steel or aluminium, ensuring at least an IP54 degree of protection;

          - where aluminium distribution blocks are used, they shall have a double-wall construction made of alloy sheets resistant to seawater (in accordance with ISO 5052/5754). Stainless steel terminal boxes shall have a sheet thickness of not less than 2 mm, and the material shall comply with the requirements of EN 1.4301 standard. All screws shall be made of stainless steel;

          - terminal blocks for current, voltage and RPA circuits shall be detachable. They shall be equipped with an integrated socket allowing a 4 mm² test wire to be inserted from both sides – for example, as in a URTK/S series terminal. For isolator control and additional information, it is recommended to use UT6-type terminals or equivalent solutions;

          - special shunt bridges, located in the middle of the terminal, must be used to connect the terminals to each other (shunting). If another type of terminal is intended to be used, this shall be agreed with the customer in advance;

          - if circuit breakers, fuses or interposing relays are installed in the distribution blocks, the blocks shall be equipped with heating with temperature control, as well as ventilation openings preventing rainwater from entering the interior;

          - before starting installation works at the site, the installation schemes and material list for the designed distribution blocks shall be agreed with the Customer.

      - Requirements for cable entry and protection in outdoor switchgear (OSG):

          - each secondary cable shall be introduced into the outdoor switchgear through a separate cable gasket. Mechanically durable and weather-resistant tags shall be used for marking. The cable designation shall be mechanically affixed and not handwritten;

          - the cable section to the ground shall be mechanically protected by a metal sheath to a height of at least 1.5 m. The control cable designation (tag) shall not be placed on conductors from which the insulation has already been removed.

      - Requirements for marking secondary cable conductors:

          - the conductors shall be marked at both ends;

          - the marking shall indicate: the circuit number, cable number and conductor number and shall correspond to the schemes;

          - the marking shall be resistant to sunlight and moisture – suitable durable ink shall be used;

          - conductors connected to relay protection and automation (RPA) panels shall be marked using fire-resistant PVC material.

- Executable documentation

  - The Contractor shall submit to the Customer in 2 copies:

- executable measurement plans (in DWG format and as a printed copy);

- installation deeds with annexes (equipment technical data sheets);

- concealed works deeds;

- measurement and test protocols;

- factory certificates and test protocols;

- operation and maintenance instructions;

- updated scheme drawings (secondary circuits).

- Safety requirement

  - All works shall be carried out in accordance with:

- CR No. 92 “Labour Protection Requirements in Performing Construction Work”;

- CR No. 209 “Equipment Electrical Safety Regulations”;

- CR No. 1041 “Regulations on the Mandatory Energy Standard Establishing Organisational and Technical Safety Requirements for the Operation of Power Supply Facilities”;

- CR No. 238 “Fire Safety Regulations”;

- CR No. 143 “Labour Protection Requirements when Working at a Height”;

- Electrical installation works may only be performed by a licensed electrical installation organisation;

- Personnel shall be certified with the appropriate electrical safety group;

  - All Laws and Regulations applicable to national security shall be complied with, including the requirements of the National Security Law of the Republic of Latvia, in particular Section 22.², Clauses 3.² and 3.³, as well as the requirements of Cabinet Regulation No. 10 of 13 January 2026 “Procedures for the Identification of Critical Infrastructure and the Planning, Implementation, and Incident Reporting of Business Continuity, Security, and Resilience Measures”, including the requirements of the National Cybersecurity Law of the Republic of Latvia and Cabinet Regulations No. 397 of 25 June 2025 “Minimum Cybersecurity Requirements” during the performance of the Contract and / or the Work, as well as when engaging personnel and subcontractors in the performance of the Work;

- Information and documentation included in the offer.

  - A confirmation that the offer submitted by the Tenderer covers the entire scope of work and materials specified in Annex 6, “Technical Specification” of the Regulations.

  - The transformer manufacturing deadlines.

  - The transformer delivery period (including transportation) to the object.

  - A description of the work to be performed under the procurement and a plan for organising the work.

  - Copies of the certificates, specifications, and descriptions for the offered equipment and materials, indicating the name of the supplier’s manufacturer and the country of origin.

  - the work execution schedule (by weeks).

FABRYKA Transformatorow w Zychlinie Sp. z o.o. Catalogue data sheet TOc 63000/115F